## UC PCS
Register Address（HEX） | Data Type | Data Meaning | Value Type | Coefficient | Unit | Remark | Note | Module
0x0101 | RO | Unit work state | u16 | N/A | N/A | Bit0:Reserved |  | UC
Bit1:Stop
Bit2:PV Charging
Bit3:Standby
Bit4:Running
Bit5:Fault
Bit6:Debug
0x0102 | RO | Unit ctrl mode | u16 | N/A | N/A | Bit0:Remote | "Local Manual" is manual mode and response the HMI command; under "Local Auto" CESS operate automatically according to the system parameters
Bit1:Local Manual
0x0103 | RO | Unit work mode | u16 | N/A | N/A | Bit9：P/Q（Remote dispatch） | PQ mode is remote control mode. this mode response the start, stop command from the user and also the target power
0x0104 | RO | Battery Maintenance State | u16 | N/A | N/A | 0:OFF 1:ON | ON:Operation; Battery maintenance state: when the battery is less than 5% soc, the system charge to the battery automatically, 1:ON is currently charging the battery, the process is automatically completed by the system, without the operation of the user; when the battery is higher than 10% SOC, the system stop charging automatically, the state clear to 0
0x0105 | RO | PCS Work State | u16 | N/A | N/A | Bit0：Initial |  | PCS
Bit1：Fault
Bit2：Stop
Bit3：Standby
Bit4：Grid Monitoring
Bit5：Ready
Bit6：Running
Bit7：Debug
0x0106 | RO | Unit ON/OFF Grid | u16 | N/A | N/A | 1:OFF 2:ON |  | UC
0x0108 | RO | Modbusprotocol version | u16 | N/A | N/A |  | Version format is vA.B；A=Value/256；B=Value%256，for example The value is 345，so The version is v1.89
0x0109 | RO | System manufacturer (BYD) | u16 | N/A | N/A | 1:BYD
0x010A | RO | System type (CESS) | u16 | N/A | N/A | 1:CESS
0x0110 | RO | suggestive information | u16 | N/A | N/A | Bit0-Bit1：Reserved | 1:appear; 0:disappear | UC
Bit2：Emergency stop
Bit3-Bit5:Reserved
Bit6：The key switch stop
Bit7-Bit15:Reserved
0x0111 | RO | suggestive information | u16 | N/A | N/A | Bit0:Reserved | 1:appear; 0:disappear
Bit1:Reserved
Bit2:Reserved
Bit3:Transformer phase B temperature sensor invalidation
Bit4:Reserved
Bit5:Reserved
Bit6:Reserved
Bit7:Reserved
Bit8:Reserved
Bit9:Reserved
Bit10:Reserved
Bit11:Reserved
Bit12:SD memory card invalidation
Bit13:Reserved
Bit14:Reserved
Bit15:Reserved
0x0125 | RO | Suggestive information | u16 | N/A | N/A | Bit0:Inverter communication abnormity | 1:appear; 0:disappear | UC
Bit1:Battery stack communication abnormity
Bit2:Multifunctional ammeter communication abnormity
Bit3:Reserved
Bit4:Remote communication abnormity
Bit5:Reserved
Bit6:Reserved
Bit7:Reserved
Bit8:Reserved
Bit9:Reserved
Bit10-Bit15:Reserved
0x0126 | RO | Suggestive information | u16 | N/A | N/A | Bit0:Reserved
Bit1:Reserved
Bit2:Reserved
Bit3:Transformer severe overtemperature
Bit4-15:Reserved
0x0150 | RO | Switch state | u16 | N/A | N/A | Bit0:Reserved | 1:closed 0:open | PCS
Bit1:DC main contactor state
Bit2:DC precharge contactor state
Bit3:AC breaker state
Bit4:AC main contactor state
Bit5:AC precharge contactor state
Bit6-Bit15:Reserved
0x180 | RO | Abnormity | u16 | N/A | N/A | Bit0: DC precharge contactor close unsuccessfully | 1:appear; 0:disappear | PCS
Bit1: AC precharge contactor close unsuccessfully
Bit2: AC main contactor close unsuccessfully
Bit3:DC electrical breaker 1 close unsuccessfully
Bit4: DC main contactor close unsuccessfully
Bit5: AC breaker trip
Bit6: AC main contactor open when running
Bit7: DC main contactor open when running
Bit8: AC main contactor open unsuccessfully
Bit9: DC electrical breaker 1 open unsuccessfully
Bit10: DC main contactor open unsuccessfully
Bit11: Hardware PDP fault
Bit12: Master stop suddenly
Bit13:Reserved
Bit14:Reserved
Bit15:Reserved
0x182 | RO | Abnormity | u16 | N/A | N/A | Bit0:DC short circuit protection | 1:appear; 0:disappear
Bit1:DC overvoltage protection
Bit2:DC undervoltage protection
Bit3:DC inverse/no connection protection
Bit4:DC disconnection protection
Bit5:Commuting voltage abnormity protection
Bit6:DC overcurrent protection
Bit7:Phase A peak current over limit protection
Bit8:Phase B peak current over limit protection
Bit9:Phase C peak current over limit protection
Bit10:Phase A virtual current over limit protection
Bit11:Phase B virtual current over limit protection
Bit12:Phase C virtual current over limit protection
Bit13:Phase A grid voltage sampling invalidation
Bit14:Phase B grid voltage sampling invalidation
Bit15:Phase C grid voltage sampling invalidation
0x183 | RO | Abnormity | u16 | N/A | N/A | Bit0:Phase A invert voltage sampling invalidation | 1:appear; 0:disappear
Bit1:Phase B invert voltage sampling invalidation
Bit2:Phase C invert voltage sampling invalidation
Bit3:AC current sampling invalidation
Bit4:DC current sampling invalidation
Bit5:Phase A overtemperature protection
Bit6:Phase B overtemperature protection
Bit7:Phase C overtemperature protection
Bit8:Phase A temperature sampling invalidation
Bit9:Phase B temperature sampling invalidation
Bit10:Phase C temperature sampling invalidation
Bit11:Phase A precharge unmet protection
Bit12:Phase B precharge unmet protection
Bit13:Phase C precharge unmet protection
Bit14:Unadaptable phase sequence error protection
Bit15:DSP protection
0x184 | RO | Abnormity | u16 | N/A | N/A | Bit0:Phase A grid voltage severe overvoltage protection | 1:appear; 0:disappear
Bit1:Phase A grid voltage general overvoltage protection
Bit2:Phase B grid voltage severe overvoltage protection
Bit3:Phase B grid voltage general overvoltage protection
Bit4:Phase C grid voltage severe overvoltage protection
Bit5:Phase C grid voltage general overvoltage protection
Bit6:Phase A grid voltage severe undervoltage protection
Bit7:Phase A grid voltage general undervoltage protection
Bit8:Phase B grid voltage severe undervoltage protection
Bit9:Phase B grid voltage general undervoltage protection
Bit10:Phase C grid voltage severe undervoltage protection
Bit11:Phase C grid voltage general undervoltage protection
Bit12:Severe overfrequency protection
Bit13:General overfrequency protection
Bit14:Severe under frequency protection
Bit15:General under frequency protection
0x185 | RO | Abnormity | u16 | N/A | N/A | Bit0:Phase A gird loss | 1:appear; 0:disappear
Bit1:Phase B gird loss
Bit2:Phase C gird loss
Bit3:Islanding protection
Bit4:Phase A under voltage ride through
Bit5:Phase B under voltage ride through
Bit6:Phase C under voltage ride through
Bit7：Phase A Inverter voltage severe overvoltage protection
Bit8：Phase A Inverter voltage general overvoltage protection
Bit9：Phase B Inverter voltage severe overvoltage protection
Bit10：Phase B Inverter voltage general overvoltage protection
Bit11：Phase C Inverter voltage severe overvoltage protection
Bit12：Phase C Inverter voltage general overvoltage protection
Bit13：Inverter peak voltage high protection cause by AC disconnect
Bit14-Bit15：Reserved
0x186 | RO | Suggestive information | u16 | N/A | N/A | Bit0:DC precharge contactor inspection abnormity | 1:appear; 0:disappear
Bit1:DC breaker 1 inspection abnormity
Bit2:DC breaker 2 inspection abnormity
Bit3:AC precharge contactor inspection abnormity
Bit4:AC main contactor inspection abnormity
Bit5:AC breaker inspection abnormity
Bit6:DC breaker 1 close unsuccessfully
Bit7:DC breaker 2 close unsuccessfully
Bit8:Control signal close abnormally inspected by system
Bit9:Control signal open abnormally inspected by system
Bit10:Neutral wire contactor close unsuccessfully
Bit11:Neutral wire contactor open unsuccessfully
Bit12:Work door open
Bit13:Emergency stop
Bit14:AC breaker close unsuccessfully
Bit15:Control switch stop
0x187 | RO | Suggestive information | u16 | N/A | N/A | Bit0:General overload | 1:appear; 0:disappear
Bit1:Severe overload
Bit2:Battery current over limit
Bit3:Power decrease caused by overtemperature
Bit4:Inverter general overtemperature
Bit5:AC three-phase current unbalance
Bit6:Rstore factory setting unsuccessfully
Bit7:Pole-board invalidation
Bit8:Self-inspection failed
Bit9:Receive BMS fault and stop
Bit10:Refrigeration equipment invalidation
Bit11:Large temperature difference among IGBT three phases
Bit12：EEPROM parameters over range
Bit13：EEPROM parameters backup failed
Bit14:DC breaker close unsuccessfully
Bit15:Reserved
0x188 | RO | Suggestive information | u16 | N/A | N/A | Bit0:Communication between inverter and BSMU disconnected | 1:appear; 0:disappear
Bit1:Communication between inverter and Master disconnected
Bit2:Communication between inverter and UC disconnected
Bit3:BMS start overtime controlled by PCS
Bit4:BMS stop overtime controlled by PCS
Bit5:Sync signal invalidation
Bit6:Sync signal continuous caputure fault
Bit7:Sync signal several times caputure fault
Bit8-Bit15：Reserved
0x0200 | RO | DC Voltage | i16 | 0.1 | V |  |  | PCS
0x0201 | RO | DC Current | i16 | 0.1 | A
0x0202 | RO | DC Power | i16 | 0.1 | kW
0x0208 | RO | DCAC AC Charge Energy(LSW) | u16 | 0.1 | kWh |  |  | PCS
0x0209 | RO | DCAC AC Charge Energy(MSW) | u16 | 0.1 | kWh
0x020A | RO | DCAC AC DisCharge Energy(LSW) | u16 | 0.1 | kWh
0x020B | RO | DCAC AC DisCharge Energy(MSW) | u16 | 0.1 | kWh
0x0210 | RO | P | i16 | 0.1 | kW |  |  | UC
0x0211 | RO | Q | i16 | 0.1 | kVar
0x0212 | RO | S | u16 | 0.1 | kVA
0x0213 | RO | Ia | i16 | 0.1 | A
0x0214 | RO | Ib | i16 | 0.1 | A
0x0215 | RO | Ic | i16 | 0.1 | A
0x0219 | RO | Ua | u16 | 0.1 | V
0x021A | RO | Ub | u16 | 0.1 | V
0x021B | RO | Uc | u16 | 0.1 | V
0x021C | RO | Frequency | u16 | 0.01 | HZ
0x0230 | RO | Allowable charging power | i16 | 0.1 | kW
0x0231 | RO | Allowable discharge power | u16 | 0.1 | kVar
0x0232 | RO | Allowable apparent power | u16 | 0.1 | kVA
0x0240 | RO | IPM Phase A temperature | i16 | 1 | ℃ |  |  | PCS
0x0241 | RO | IPM Phase B temperature | i16 | 1 | ℃
0x0242 | RO | IPM Phase C temperature | i16 | 1 | ℃
0x0249 | RO | Transformer Phase B temperature | i16 | 1 | ℃ |  |  | UC
0x0300 | RO | TotalEnergy（LSW） | u16 | 1 | kWh |  |  | UC
0x0301 | RO | TotalEnergy（MSW） | u16 | 1 | kWh
0x0302 | RO | TotalYearEnergy（LSW） | u16 | 1 | kWh
0x0303 | RO | TotalYearEnergy（MSW） | u16 | 1 | kWh
0x0304 | RO | TotalMonthEnergy（LSW） | u16 | 1 | kWh
0x0305 | RO | TotalMonthEnergy（MSW） | u16 | 1 | kWh
0x0306 | RO | TotalDateEnergy | u16 | 1 | kWh
0x0307 | RO | TotalHourEnergy_0 | u16 | 1 | kWh
0x0308 | RO | TotalHourEnergy_1 | u16 | 1 | kWh
0x0309 | RO | TotalHourEnergy_2 | u16 | 1 | kWh
0x030A | RO | TotalHourEnergy_3 | u16 | 1 | kWh
0x030B | RO | TotalHourEnergy_4 | u16 | 1 | kWh
0x030C | RO | TotalHourEnergy_5 | u16 | 1 | kWh
0x030D | RO | TotalHourEnergy_6 | u16 | 1 | kWh
0x030E | RO | TotalHourEnergy_7 | u16 | 1 | kWh
0x030F | RO | TotalHourEnergy_8 | u16 | 1 | kWh
0x0310 | RO | TotalHourEnergy_9 | u16 | 1 | kWh
0x0311 | RO | TotalHourEnergy_10 | u16 | 1 | kWh
0x0312 | RO | TotalHourEnergy_11 | u16 | 1 | kWh
0x0313 | RO | TotalHourEnergy_12 | u16 | 1 | kWh
0x0314 | RO | TotalHourEnergy_13 | u16 | 1 | kWh
0x0315 | RO | TotalHourEnergy_14 | u16 | 1 | kWh
0x0316 | RO | TotalHourEnergy_15 | u16 | 1 | kWh
0x0317 | RO | TotalHourEnergy_16 | u16 | 1 | kWh
0x0318 | RO | TotalHourEnergy_17 | u16 | 1 | kWh
0x0319 | RO | TotalHourEnergy_18 | u16 | 1 | kWh
0x031A | RO | TotalHourEnergy_19 | u16 | 1 | kWh
0x031B | RO | TotalHourEnergy_20 | u16 | 1 | kWh
0x031C | RO | TotalHourEnergy_21 | u16 | 1 | kWh
0x031D | RO | TotalHourEnergy_22 | u16 | 1 | kWh
0x031E | RO | TotalHourEnergy_23 | u16 | 1 | kWh
0x0500 | RW | Work state control command | u16 | N/A | N/A | Bit2:Stop |  | UC
Bit6:Run
0x501 | RW | Active power command | i16 | 0.1 | kW |  | postive:discharge negative:charge
0x502 | RW | Reactive power command | i16 | 0.1 | kvar |  | postive:provides reactive negative:absorbs reactive
0x0601 | RW | Work mode control command | u16 | N/A | N/A | Bit9：P/Q（Remote dispatch） | The default mode is remote power dispatch. It is allowed to write only the Bit9. | UC

## BMS
Register Address（HEX） | Data Type | Data Meaning | Value Type | Coefficient | Unit | Remark | Note
0x1100 | RO | Battery string work state | u16 | N/A | N/A | Bit0:Initial
Bit1:Stop
Bit2:Starting up
Bit3:Running
Bit4:Fault
0x1101 | RO | Battery string switch state | u16 | N/A | N/A | bit0:Main contactor | 1:closed ；0:open
bit1:Precharge contactor
bit2:FAN contactor
bit3:BMU power supply relay
bit4:Middle relay
Bit5-bit15:Reserved
0x1102 | RO | Battery string peripheral IO state | u16 | N/A | N/A | bit0:Fuse state | 1:closed ；0:open
bit4:iIsolated switch state
bit5-bit15:Reserved
0x1103 | RO | Battery string suggestive information | u16 | N/A | N/A | Bit0:Battery string charge general overcurrent | 1:appear 0:disappear
Bit1:Battery string discharge general overcurrent
Bit2:Battery string charge current over limit
Bit3:Battery string discharge current over limit
Bit4:Battery string general overvoltage
Bit5:Battery string general undervoltage
Bit6:Reserved
Bit7:Battery string general over temperature
Bit8:Battery string general under temperature
Bit9:Reserved
Bit10:Battery string severe overvoltage
Bit11:Battery string severe under voltage
Bit12:Battery string severe under temperature
Bit13:Battery string charge severe overcurrent
Bit14:Battery string discharge severe overcurrent
Bit15:Battery string capacity abnormity
0x1105 | RO | Battery string abnormity | u16 | N/A | N/A | Bit0:Reserved | 1:appear 0:disappear
Bit1:Reserved
Bit2:Battery string voltage sampling route invalidation
Bit3:Reserved
Bit4:Battery string voltage sampling route disconnected
Bit5:Battery string temperature sampling route disconnected
Bit6:Battery string inside CAN disconnected
Bit7:Reserved
Bit8:Reserved
Bit9:Battery string current sampling circuit abnormity
Bit10:Battery string battery cell invalidation
Bit11:Battery string main contactor inspection abnormity
Bit12:Battery string precharge contactor inspection abnormity
Bit13:Battery string negative contactor inspection abnormity
Bit14:Battery string power supply relay inspection abnormity
Bit15:Battery string middle relay abnormity
0x1106 | RO | Battery string abnormity | u16 | N/A | N/A | Bit0:Reserved | 1:appear 0:disappear
Bit1:Reserved
Bit2:Battery string severe overtemperature
Bit3:Reserved
Bit4:Reserved
Bit5:Reserved
Bit6:Reserved
Bit7:Battery string smog fault
Bit8:Battery string blown fuse indicator fault
Bit9:Reserved
Bit10:Battery string general leakage
Bit11:Battery string severe leakage
Bit12:Communication between BECU and periphery CAN disconnected
Bit13:Reserved
Bit14:Battery string power supply relay contactor disconnected
Bit15:Reserved
0x1400 | RO | Battery string total voltage | u16 | 0.1 | V
0x1401 | RO | Battery string total current | i16 | 0.1 | A
0x1402 | RO | Battery string SOC | u16 | 1 | %
0x1403 | RO | Battery string SOH | u16 | 1 | %
0x1404 | RO | Battery string cell average temperature | i16 | 1 | ℃
0x1406 | RO | Battery string charge current limit | u16 | 0.1 | A
0x1407 | RO | Battery string discharge current limit | u16 | 0.1 | A
0x140A | RO | Battery string charge/discharge times（LSW） | u16 | 1 | N/A
0x140B | RO | Battery string charge/discharge times（MSW） | u16 | 1 | N/A
0x1418 | RO | Battery string accumulated charge energy（LSW） | u16 | 1 | Wh
0x1419 | RO | Battery string accumulated charge energy（MSW） | u16 | 1 | Wh
0x141A | RO | Battery string accumulated discharge energy（LSW） | u16 | 1 | Wh
0x141B | RO | Battery string accumulated discharge energy（MSW） | u16 | 1 | Wh
0x1420 | RO | Battery Power | i16 | 0.1 | kW | Battery output power
0x1430 | RO | Battery string Max cell voltage battery NO. | u16 | 1 | N/A
0x1431 | RO | Battery string Max cell voltage | u16 | 0.001 | V
0x1432 | RO | Temperature of Battery string Max voltage cell | i16 | 1 | ℃
0x1433 | RO | Battery string Min cell voltage battery NO. | u16 | 1 | N/A
0x1434 | RO | Battery string Min cell voltage | u16 | 0.001 | V
0x1435 | RO | Temperature of Battery string Min voltage cell | i16 | 1 | ℃
0x143A | RO | Battery string Max cell temperature battery NO. | u16 | 1 | N/A
0x143B | RO | Battery string Max cell temperature | i16 | 1 | ℃
0x143C | RO | Voltage of Battery string Max temperature cell | u16 | 0.001 | V
0x143D | RO | Battery string Min cell temperature battery NO. | u16 | 1 | N/A
0x143E | RO | Battery string Min cell temperature | i16 | 1 | ℃
0x143F | RO | Voltage of Battery string Min temperature cell | u16 | 0.001 | V
0x1500~0x16FF | RO | Battery string cell voltage | u16 | 0.001 | V | 1~64
0x1700~0x18FF | RO | Battery string cell temperature | i16 | 1 | ℃ | 1~64

## log
序号 | 内容 | 版本 | 修改人
1 | 初版 | V001.00 | 马明君
2 | 增加累计电能 | V001.01 | 马明君
3 | 增加PV总输出功率 | V001.02 | 马明君
4 | 增加DCDC告警 | V001.03 | 杨荣春
5 | 修改DCDC累计电量地址 | V001.04 | 马明君
6 | 增加削峰填谷模式时间及功率地址 | V001.05 | 马明君
7 | 增加GMLO\GMLP模式及相关控制 | V001.06 | 马明君
8 | 修改系统工作状态，增加PCS工作状态 | V001.07 | 马明君
9 | 在系统中增加电池容量测量模式和模式相关的设置 | V001.08 | 杨荣春
10 | 增加柴油机模式和运行参数 | V001.09 | 杨荣春
11 | 增加电池输出功率和系统并离网状态显示 | V001.10 | 杨荣春
12 | 修改PCS及BMS告警及故障信息 | V001.11 | 马明君
13 | 增加功率目标地址 | V001.12 | 马明君
14 | 删除DCDC信息，美版 | V001.13 | 马明君
15 | 新增允许充放电功率，协议版本，厂家，系统类型地址 | V001.14 | 马明君