## MINI Protocol
Modbus Device ID: 4 | MINIES Communication Protocol
Register classification | Register Address (Decimal) | Register type | Value Type | Register Defination | Detail | Range | Mark
Status Register | 100 | RO | u16 | System Status | 0:Standby | 0-4
1:Off-grid
2:On-grid
3:Fail
4:Off-grid PV
| 101 | RO | u16 | Control Mode | 1:Remote | 1,2 | customer can dispatch orders only in remote control mode.
2:Local
| 102 | RO | u16 | Work Mode | 2:Economy
6:Remote dispatch
8:Timing
| 104 | RO | u16 | Battery total electric energy of charging(0~15bit) | 1Wh | 0-65535
| 105 | RO | u16 | Battery total electric energy of charging(16~31bit) | 1Wh | 0-65535
| 106 | RO | u16 | Battery total electric energy of discharging (0~15bit) | 1Wh | 0-65535
| 107 | RO | u16 | Battery total electric energy of discharging (16~31bit) | 1Wh | 0-65535
| 108 | RO | u16 | Battery group status | 0::nitial | 0-5
1:Stop
2:Starting
3:Running
4:Stopping
5:Fail
| 109 | RO | u16 | Battery group SOC | 1% | 0-100
| 110 | RO | u16 | Battery group voltage | 0.1V
| 111 | RO | s16 | Battery group current | 0.1A
| 112 | RO | s16 | Battery group power | 1W
| 113 | RO | u16 | Battery group alarm message | Bit0:Fail, The system should be stopped | 0:Normal 1: The system should be stoped
[5 empty] | Bit1: Common low voltage alarm | 0:Normal 1:Common low voltage | No discharging allowed(need to be done by customer)
[5 empty] | Bit2:Common high voltage alarm | 0:Normal 1:Common high voltage | No charging allowed(need to be done by customer)
[5 empty] | Bit3:Charging over current alarm | 0:Normal 1: Charging over current | system will lower the power
[5 empty] | Bit4:Discharging over current alarm | 0:Normal 1:Discharging over current | system will lower the power
[5 empty] | Bit5:Over temperature alarm | 0:Normal1:Over temperature | system will lower the power
[5 empty] | Bit6:Interal communication abnormal | 0:Normal1:Interal communication abnormal | Please check the internal communication cable connection
[5 empty] | Bit7-Bit15:Reserve | Reserve
| 114 | RO | u16 | PCS Operation Status | 0:Self-checking | 0~7
1:Standby
2:Off grid PV
3:Off grid
4:On grid
5:Fail
6:bypass 1
7:bypass 2
| 118 | RO | s16 | Output current of phase A | 0.1A |  | Inverter output
| 119 | RO | s16 | Output current of phase B | 0.1A
| 120 | RO | s16 | Output current of phase C | 0.1A
| 121 | RO | u16 | Voltage of Grid phase A | 0.1V
| 122 | RO | u16 | Voltage of Grid phase B | 0.1V
| 123 | RO | u16 | Voltage of Grid phase C | 0.1V
| 124 | RO | s16 | Active power of phase A | 1W |  | Inverter output
| 125 | RO | s16 | Active power of phase B | 1W
| 126 | RO | s16 | Active power of phase C | 1W
| 127 | RO | s16 | Reactive power of phase A | 1var |  | Inverter output
| 128 | RO | s16 | Reactive power of phase B | 1var
| 129 | RO | s16 | Reactive power of phase C | 1var
| 131 | RO | u16 | Grid frequency of phase A | 0.01Hz
| 132 | RO | u16 | Grid frequency of phase B | 0.01Hz
| 133 | RO | u16 | Grid frequency of phase C | 0.01Hz
| 134 | RO | u16 | PCS maximum output apparent power | 1W |  | PCS maximum power output ability
| 139 | R0 | s16 | Total active power of meter | 1W |  | Total active power of meter
| 140 | RO | s16 | Total reactive Power of meter | 1var |  | Total reactive power of meter
| 141 | RO | u16 | System charging power limitation | 1W |  | Inverter output
| 142 | RO | u16 | System discharging power limitation | 1W |  | Inverter output
| 143 | RO | u16 | PV inverter power of phase A | 1W
| 144 | RO | u16 | PV inverter power of phase B | 1W
| 145 | RO | u16 | PV inverter power of phase C | 1W
| 150 | RO | u16 | PCS alarm message1 of phase A | Bit0:Grid undervoltage
Bit1:Grid overvoltage
Bit2:Grid under frequency
Bit3:Grid over frequency
Bit4:Grid power supply off
Bit5:Grid condition unmeet
Bit6:DC under voltage
Bit7:Input over resistance
Bit8:Combination error
Bit9:Comm with inverter error
Bit10:Tme error
Bit11-Bit15:Reserved
| 151 | RO | u16 | PCS alarm message2 of phase A | Bit0-Bit15:Reserved
| 152 | RO | u16 | PCS fault message1 of phase A | Bit0:Control current overload 100%
Bit1:Control current overload 110%
Bit2:Control current overload 150%
Alarm Register |  |  |  |  | Bit3:Control current overload 200%
Bit4:Control current overload 120%
Bit5:Control current overload 300%
Bit6:Control transient load 300%
Bit7:Grid over current
Bit8:Locking waveform too many times
Bit9:Inverter voltage zero drift error
Bit10:Grid voltage zero drift error
Bit11:Control current zero drift error
Bit12:Inverter current zero drift error
Bit13:Grid current zero drift error
Bit14:PDP protection
Bit15:Hardware control current protection
| 153 | RO | u16 | PCS fault message2 of phase A | Bit0:Hardware AC volt. protection
Bit1:Hardware DC curr. protection
Bit2:Hardware temperature protection
Bit3:No capturing signal
Bit4:DC overvoltage
Bit5:DC disconnected
Bit6:Inverter undervoltage
Bit7:Inverter overvoltage
Bit8:Current sensor fail
Bit9:Voltage sensor fail
Bit10:Power uncontrollable
Bit11:Current uncontrollable
Bit12:Fan error
Bit13:Phase lack
Bit14:Inverter relay fault
Bit15:Grid relay fault
| 154 | RO | u16 | PCS fault message3 of phase A | Bit0:Control panel overtemp
Bit1:Power panel overtemp
Bit2:DC input overcurrent
Bit3:Capacitor overtemp
Bit4:Radiator overtemp
Bit5:Transformer overtemp
Bit6:Combination comm error
Bit7:EEPROM error
Bit8:Load current zero drift error
Bit9:Current limit-R error
Bit10:Phase sync error
Bit11:External PV current zero drift error
Bit12:External grid current zero drift error
Bit13-Bit15:Reserved
| 155 | RO | u16 | PCS alarm message1 of phase B | Bit0:Grid undervoltage
Bit1:Grid overvoltage
Bit2:Grid under frequency
Bit3:Grid over frequency
Bit4:Grid power supply off
Bit5:Grid condition unmeet
Bit6:DC under voltage
Bit7:Input over resistance
Bit8:Combination error
Bit9:Comm with inverter error
Bit10:Tme error
Bit11-Bit15:Reserved
| 156 | RO | u16 | PCS alarm message2 of phase B | Bit0-Bit15:Reserved
| 157 | RO | u16 | PCS fault message1 of phase B | Bit0:Control current overload 100%
Bit1:Control current overload 110%
Bit2:Control current overload 150%
Bit3:Control current overload 200%
Bit4:Control current overload 120%
Bit5:Control current overload 300%
Bit6:Control transient load 300%
Bit7:Grid over current
Bit8:Locking waveform too many times
Bit9:Inverter voltage zero drift error
Bit10:Grid voltage zero drift error
Bit11:Control current zero drift error
Bit12:Inverter current zero drift error
Bit13:Grid current zero drift error
Bit14:PDP protection
Bit15:Hardware control current protection
| 158 | RO | u16 | PCS fault message2 of phase B | Bit0:Hardware AC volt. protection
Bit1:Hardware DC curr. protection
Bit2:Hardware temperature protection
Bit3:No capturing signal
Bit4:DC overvoltage
Bit5:DC disconnected
Bit6:Inverter undervoltage
Bit7:Inverter overvoltage
Bit8:Current sensor fail
Bit9:Voltage sensor fail
Bit10:Power uncontrollable
Bit11:Current uncontrollable
Bit12:Fan error
Bit13:Phase lack
Bit14:Inverter relay fault
Bit15:Grid relay fault
| 159 | RO | u16 | PCS fault message3 of phase B | Bit0:Control panel overtemp
Bit1:Power panel overtemp
Bit2:DC input overcurrent
Bit3:Capacitor overtemp
Bit4:Radiator overtemp
Bit5:Transformer overtemp
Bit6:Combination comm error
Bit7:EEPROM error
Bit8:Load current zero drift error
Bit9:Current limit-R error
Bit10:Phase sync error
Bit11:External PV current zero drift error
Bit12:External grid current zero drift error
Bit13-Bit15:Reserved
| 160 | RO | u16 | PCS alarm message1 of phase C | Bit0:Grid undervoltage
Bit1:Grid overvoltage
Bit2:Grid under frequency
Bit3:Grid over frequency
Bit4:Grid power supply off
Bit5:Grid condition unmeet
Bit6:DC under voltage
Bit7:Input over resistance
Bit8:Combination error
Bit9:Comm with inverter error
Bit10:Tme error
Bit11-Bit15:Reserved
| 161 | RO | u16 | PCS alarm message2 of phase C | Bit0-Bit15:Reserved
| 162 | RO | u16 | PCS fault message1 of phase C | Bit0:Control current overload 100%
Bit1:Control current overload 110%
Bit2:Control current overload 150%
Bit3:Control current overload 200%
Bit4:Control current overload 120%
Bit5:Control current overload 300%
Bit6:Control transient load 300%
Bit7:Grid over current
Bit8:Locking waveform too many times
Bit9:Inverter voltage zero drift error
Bit10:Grid voltage zero drift error
Bit11:Control current zero drift error
Bit12:Inverter current zero drift error
Bit13:Grid current zero drift error
Bit14:PDP protection
Bit15:Hardware control current protection
| 163 | RO | u16 | PCS fault message2 of phase C | Bit0:Hardware AC volt. protection
Bit1:Hardware DC curr. protection
Bit2:Hardware temperature protection
Bit3:No capturing signal
Bit4:DC overvoltage
Bit5:DC disconnected
Bit6:Inverter undervoltage
Bit7:Inverter overvoltage
Bit8:Current sensor fail
Bit9:Voltage sensor fail
Bit10:Power uncontrollable
Bit11:Current uncontrollable
Bit12:Fan error
Bit13:Phase lack
Bit14:Inverter relay fault
Bit15:Grid relay fault
| 164 | RO | u16 | PCS fault message3 of phase C | Bit0:Control panel overtemp
Bit1:Power panel overtemp
Bit2:DC input overcurrent
Bit3:Capacitor overtemp
Bit4:Radiator overtemp
Bit5:Transformer overtemp
Bit6:Combination comm error
Bit7:EEPROM error
Bit8:Load current zero drift error
Bit9:Current limit-R error
Bit10:Phase sync error
Bit11:External PV current zero drift error
Bit12:External grid current zero drift error
Bit13-Bit15:Reserved
Control Register | 200 | WR | u16 | System control | 0:Local contol |  | Not support
[5 empty] | 1:Remote control on grid starting |  | System will start after receiving this command in the shutdown or stop state
[5 empty] | 2:Remote control off grid starting |  | Not support
[5 empty] | 3:Stop |  | System will stop,power of important loads supplied by grid
[5 empty] | 4:shutdown |  | System will shutdown, important loads will loss power supply
| 206 | WR | s16 | Target active power of phase A | 1W
| 207 | WR | s16 | Target reactive power of phase A | 1var
| 208 | WR | s16 | Target active power of phase B | 1W
| 209 | WR | s16 | Target reactive power of phase B | 1var
| 210 | WR | s16 | Target active power of phase C | 1W
| 211 | WR | s16 | Target reactive power of phase C | 1var
Note: 1.When the operation mode is remote control mode, and the remote indicator light is on, the system could be controlled remotely 2.If the control registers(adress 206~211) aren't been updated within 60s,the system will swicth to local control mode automatically.

## Control method
Function | Steps |  | Details
Start control | 1 | Confirm the control mode is"Remote":Read register"101"and the number is "1" | Press the "Remote"button for five seconds
| 2 | Confirm the system status is"Standby ":Read register"100" and the number is "0" | Write in "3"to register"200"
| 3 | Send start commad:Write in "1"to register"200"
| 4 | Confirm system status is "On-grid": Read register"100"and the number is "2"
| 5 | The system start command finished
Stop control | 1 | Confirm the control mode is"Remote":Read register"101"and the number is "1" | Press the "Remote"button for five seconds
| 2 | Send stop commad:Write in "3"to register"200"
| 3 | Confirm system status is"standby": Read register"100"and the number is "0"
| 4 | The system stop command finished
Power regulation control | 1 | Confirm the control mode is"Remote":Read register"101"and the number is "1" | Press the "Remote"button for five seconds
| 2 | Confirm system status is "On-grid": Read register"100"and the number is "2"
| 3 | Send phase A target power: Write active power number to register"206" and reactive power to register"207".Phase B target power registers are "208"and"209",and phase C are "210"and"211".
| 4 | The power control command finished

## Log
N0. | Description | Ver. | Modifier | Date
1 | First release of Modbus Register List | V001.00 | Yangrongchun | 2016-04-17
2 | Add log sheet | V001.01 | Qinxiqun | 2016-04-19
3 | Add work mode | V001.02 | Qinxiqun | 2016-04-27
4 | Add triphase registers | V001.03 | Qinxiqun | 2016-04-27
5 | Add control method description | V001.04 | Qinxiqun | 2016-06-01
6 | Add PCS alarm | V001.05 | Qinxiqun | 2016-08-24
7 | Modify register type of control data | V001.06 | Qinxiqun | 2016-10-12