## Index
Model | Label | Description | Notes
64204 | Q(U) extended | All SunSpec compliant devices must include this as the first model
SunSpec Model is unsupported / Element of SunSpec model is NOT implemented
SunSpec Model is supported / Element of SunSpec model is implemented
Element of SunSpec model is implemented, but may not be written periodically
Element of SunSpec model is implemented only for special inverter models/configurations

## 64204
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Q(U) extended | 64204 | uint16 |  |  | R | M | Q(U) offset extension
Header |  | 1 |  | 1 | L |  | 8 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | VerMajor | Version Information of Model | 1 | uint16 |  |  | R | M | Major Version number
Fixed Block |  | 3 | 1 | 1 | VerMinor |  | 0 | uint16 |  |  | R | M | Minor Version number
Fixed Block |  | 4 | 2 | 1 | VOffPct |  |  | int16 | %VRef | VOffPct_SF | RW | M | Q(U) grid voltage offset
Fixed Block |  | 5 | 3 | 1 | VArOffPct |  |  | int16 | %refVal | VArOffPct_SF | RW | M | Q(U) reactive power offset (The depending reference is configured in model 126. %refVal is %Wmax, %VArMax or %VArAval depending on value of DeptRef in model 126)
Fixed Block |  | 6 | 4 | 1 | RvrtTms | RvrtTms |  | uint16 | Secs |  | RW | M | Timeout period for volt-VAR curve selection
Fixed Block |  | 7 | 5 | 1 | OffsetEna | OffsetEna |  | enum16 |  |  | RW | M | Q(U) dynamic Q/U offset enable
Fixed Block |  | 8 | 6 | 1 | VOffPct_SF | VOffPct_SF |  | sunssf |  |  | R | M | Scale factor for offset voltage
Fixed Block |  | 9 | 7 | 1 | VArOffPct_SF | VArOffPct_SF |  | sunssf |  |  | R | M | Scale factor for reactive power offset
enum16 | OffsetEna |  |  |  | DISABLED |  | 0
enum16 | OffsetEna |  |  |  | ENABLED |  | 1