## UC PCS DCDC
Register Address（HEX） | Data Type | Data Meaning | Value Type | Coefficient | Unit | Remark | Note | Module
0x0101 | RO | Unit work state | u16 | N/A | N/A | Bit0:Reserved |  | UC
Bit1:Stop
Bit2:PV Charging
Bit3:Standby
Bit4:Running
Bit5:Fault
Bit6:Debug
0x0102 | RO | Unit ctrl mode | u16 | N/A | N/A | Bit0:Remote
Bit1:Local Manual
0x0103 | RO | Unit work mode | u16 | N/A | N/A | Bit9：P/Q（Remote dispatch）
0x0104 | RO | Battery Maintenance State | u16 | N/A | N/A | 0:OFF 1:ON | ON:Operation
0x0105 | RO | PCS Work State | u16 | N/A | N/A | Bit0：Initial |  | PCS
Bit1：Fault
Bit2：Stop
Bit3：Standby
Bit4：Grid Monitoring
Bit5：Ready
Bit6：Running
Bit7：Debug
0x0106 | RO | Unit ON/OFF Grid | u16 | N/A | N/A | 1:OFF 2:ON |  | UC
0x0108 | RO | Modbusprotocol version | u16 | N/A | N/A |  | Version format is vA.B；A=Value/256；B=Value%256，for example The value is 345，so The version is v1.89
0x0109 | RO | System manufacturer (BYD) | u16 | N/A | N/A | 1:BYD
0x010A | RO | System type (CESS) | u16 | N/A | N/A | 1:CESS
0x0110 | RO | suggestive information | u16 | N/A | N/A | Bit0-Bit1：Reserved | 1:appear; 0:disappear | UC
Bit2：Emergency stop
Bit3-Bit5:Reserved
Bit6：The key switch stop
Bit7-Bit15:Reserved
0x0111 | RO | suggestive information | u16 | N/A | N/A | Bit0:Reserved | 1:appear; 0:disappear
Bit1:Reserved
Bit2:Reserved
Bit3:Transformer phase B temperature sensor invalidation
Bit4:Reserved
Bit5:Reserved
Bit6:Reserved
Bit7:Reserved
Bit8:Reserved
Bit9:Reserved
Bit10:Reserved
Bit11:Reserved
Bit12:SD memory card invalidation
Bit13:Reserved
Bit14:Reserved
Bit15:Reserved
0x0125 | RO | Suggestive information | u16 | N/A | N/A | Bit0:Inverter communication abnormity | 1:appear; 0:disappear | UC
Bit1:Battery stack communication abnormity
Bit2:Multifunctional ammeter communication abnormity
Bit3:Reserved
Bit4:Remote communication abnormity
Bit5:Reserved
Bit6:Reserved
Bit7:Reserved
Bit8:Reserved
Bit9:Reserved
Bit10-Bit15:Reserved
0x0126 | RO | Suggestive information | u16 | N/A | N/A | Bit0:Reserved
Bit1:Reserved
Bit2:Reserved
Bit3:Transformer severe overtemperature
Bit4-15:Reserved
0x0150 | RO | Switch state | u16 | N/A | N/A | Bit0:Reserved | 1:closed 0:open | PCS
Bit1:DC main contactor state
Bit2:DC precharge contactor state
Bit3:AC breaker state
Bit4:AC main contactor state
Bit5:AC precharge contactor state
Bit6-Bit15:Reserved
0x0180 | RO | Abnormity | u16 | N/A | N/A | Bit0: DC precharge contactor close unsuccessfully | 1:appear; 0:disappear | PCS
Bit1: AC precharge contactor close unsuccessfully
Bit2: AC main contactor close unsuccessfully
Bit3:DC electrical breaker 1 close unsuccessfully
Bit4: DC main contactor close unsuccessfully
Bit5: AC breaker trip
Bit6: AC main contactor open when running
Bit7: DC main contactor open when running
Bit8: AC main contactor open unsuccessfully
Bit9: DC electrical breaker 1 open unsuccessfully
Bit10: DC main contactor open unsuccessfully
Bit11: Hardware PDP fault
Bit12: Master stop suddenly
Bit13:Reserved
Bit14:Reserved
Bit15:Reserved
0x0182 | RO | Abnormity | u16 | N/A | N/A | Bit0:DC short circuit protection | 1:appear; 0:disappear
Bit1:DC overvoltage protection
Bit2:DC undervoltage protection
Bit3:DC inverse/no connection protection
Bit4:DC disconnection protection
Bit5:Commuting voltage abnormity protection
Bit6:DC overcurrent protection
Bit7:Phase A peak current over limit protection
Bit8:Phase B peak current over limit protection
Bit9:Phase C peak current over limit protection
Bit10:Phase A virtual current over limit protection
Bit11:Phase B virtual current over limit protection
Bit12:Phase C virtual current over limit protection
Bit13:Phase A grid voltage sampling invalidation
Bit14:Phase B grid voltage sampling invalidation
Bit15:Phase C grid voltage sampling invalidation
0x0183 | RO | Abnormity | u16 | N/A | N/A | Bit0:Phase A invert voltage sampling invalidation | 1:appear; 0:disappear
Bit1:Phase B invert voltage sampling invalidation
Bit2:Phase C invert voltage sampling invalidation
Bit3:AC current sampling invalidation
Bit4:DC current sampling invalidation
Bit5:Phase A overtemperature protection
Bit6:Phase B overtemperature protection
Bit7:Phase C overtemperature protection
Bit8:Phase A temperature sampling invalidation
Bit9:Phase B temperature sampling invalidation
Bit10:Phase C temperature sampling invalidation
Bit11:Phase A precharge unmet protection
Bit12:Phase B precharge unmet protection
Bit13:Phase C precharge unmet protection
Bit14:Unadaptable phase sequence error protection
Bit15:DSP protection
0x0184 | RO | Abnormity | u16 | N/A | N/A | Bit0:Phase A grid voltage severe overvoltage protection | 1:appear; 0:disappear
Bit1:Phase A grid voltage general overvoltage protection
Bit2:Phase B grid voltage severe overvoltage protection
Bit3:Phase B grid voltage general overvoltage protection
Bit4:Phase C grid voltage severe overvoltage protection
Bit5:Phase C grid voltage general overvoltage protection
Bit6:Phase A grid voltage severe undervoltage protection
Bit7:Phase A grid voltage general undervoltage protection
Bit8:Phase B grid voltage severe undervoltage protection
Bit9:Phase B grid voltage general undervoltage protection
Bit10:Phase C grid voltage severe undervoltage protection
Bit11:Phase C grid voltage general undervoltage protection
Bit12:Severe overfrequency protection
Bit13:General overfrequency protection
Bit14:Severe under frequency protection
Bit15:General under frequency protection
0x0185 | RO | Abnormity | u16 | N/A | N/A | Bit0:Phase A gird loss | 1:appear; 0:disappear
Bit1:Phase B gird loss
Bit2:Phase C gird loss
Bit3:Islanding protection
Bit4:Phase A under voltage ride through
Bit5:Phase B under voltage ride through
Bit6:Phase C under voltage ride through
Bit7：Phase A Inverter voltage severe overvoltage protection
Bit8：Phase A Inverter voltage general overvoltage protection
Bit9：Phase B Inverter voltage severe overvoltage protection
Bit10：Phase B Inverter voltage general overvoltage protection
Bit11：Phase C Inverter voltage severe overvoltage protection
Bit12：Phase C Inverter voltage general overvoltage protection
Bit13：Inverter peak voltage high protection cause by AC disconnect
Bit14-Bit15：Reserved
0x0186 | RO | Suggestive information | u16 | N/A | N/A | Bit0:DC precharge contactor inspection abnormity | 1:appear; 0:disappear
Bit1:DC breaker 1 inspection abnormity
Bit2:DC breaker 2 inspection abnormity
Bit3:AC precharge contactor inspection abnormity
Bit4:AC main contactor inspection abnormity
Bit5:AC breaker inspection abnormity
Bit6:DC breaker 1 close unsuccessfully
Bit7:DC breaker 2 close unsuccessfully
Bit8:Control signal close abnormally inspected by system
Bit9:Control signal open abnormally inspected by system
Bit10:Neutral wire contactor close unsuccessfully
Bit11:Neutral wire contactor open unsuccessfully
Bit12:Work door open
Bit13:Emergency stop
Bit14:AC breaker close unsuccessfully
Bit15:Control switch stop
0x0187 | RO | Suggestive information | u16 | N/A | N/A | Bit0:General overload | 1:appear; 0:disappear
Bit1:Severe overload
Bit2:Battery current over limit
Bit3:Power decrease caused by overtemperature
Bit4:Inverter general overtemperature
Bit5:AC three-phase current unbalance
Bit6:Rstore factory setting unsuccessfully
Bit7:Pole-board invalidation
Bit8:Self-inspection failed
Bit9:Receive BMS fault and stop
Bit10:Refrigeration equipment invalidation
Bit11:Large temperature difference among IGBT three phases
Bit12：EEPROM parameters over range
Bit13：EEPROM parameters backup failed
Bit14:DC breaker close unsuccessfully
Bit15:Reserved
0x0188 | RO | Suggestive information | u16 | N/A | N/A | Bit0:Communication between inverter and BSMU disconnected | 1:appear; 0:disappear
Bit1:Communication between inverter and Master disconnected
Bit2:Communication between inverter and UC disconnected
Bit3:BMS start overtime controlled by PCS
Bit4:BMS stop overtime controlled by PCS
Bit5:Sync signal invalidation
Bit6:Sync signal continuous caputure fault
Bit7:Sync signal several times caputure fault
Bit8-Bit15：Reserved
0x0200 | RO | DC Voltage | i16 | 0.1 | V |  |  | PCS
0x0201 | RO | DC Current | i16 | 0.1 | A
0x0202 | RO | DC Power | i16 | 0.1 | kW
0x0208 | RO | DCAC AC Charge Energy(LSW) | u16 | 0.1 | kWh |  |  | PCS
0x0209 | RO | DCAC AC Charge Energy(MSW) | u16 | 0.1 | kWh
0x020A | RO | DCAC AC DisCharge Energy(LSW) | u16 | 0.1 | kWh
0x020B | RO | DCAC AC DisCharge Energy(MSW) | u16 | 0.1 | kWh
0x0210 | RO | P | i16 | 0.1 | kW |  |  | UC
0x0211 | RO | Q | i16 | 0.1 | kvar
0x0212 | RO | S | u16 | 0.1 | kVA
0x0213 | RO | Ia | i16 | 0.1 | A
0x0214 | RO | Ib | i16 | 0.1 | A
0x0215 | RO | Ic | i16 | 0.1 | A
0x0219 | RO | Ua | u16 | 0.1 | V
0x021A | RO | Ub | u16 | 0.1 | V
0x021B | RO | Uc | u16 | 0.1 | V
0x021C | RO | Frequency | u16 | 0.01 | Hz
0x021D-0x0221 | RO | Reserved
0x0222 | RO | Inverter Ua | u16 | 0.1 | V |  |  | PCS
0x0223 | RO | Inverter Ub | u16 | 0.1 | V
0x0224 | RO | Inverter Uc | u16 | 0.1 | V
0x0225 | RO | Inverter Ia | i16 | 0.1 | A
0x0226 | RO | Inverter Ib | i16 | 0.1 | A
0x0227 | RO | Inverter Ic | i16 | 0.1 | A
0x0228 | RO | Inverter Power | i16 | 0.1 | kW
0x0230 | RO | Allowable charging power | i16 | 0.1 | kW
0x0231 | RO | Allowable discharge power | u16 | 0.1 | kW
0x0232 | RO | Allowable apparent power | u16 | 0.1 | kVA
0x0240 | RO | IPM Phase A temperature | i16 | 1 | ℃ |  |  | PCS
0x0241 | RO | IPM Phase B temperature | i16 | 1 | ℃
0x0242 | RO | IPM Phase C temperature | i16 | 1 | ℃
0x0249 | RO | Transformer Phase B temperature | i16 | 1 | ℃ |  |  | UC
0x0300 | RO | TotalEnergy（LSW） | u16 | 1 | kWh |  |  | UC
0x0301 | RO | TotalEnergy（MSW） | u16 | 1 | kWh
0x0302 | RO | TotalYearEnergy（LSW） | u16 | 1 | kWh
0x0303 | RO | TotalYearEnergy（MSW） | u16 | 1 | kWh
0x0304 | RO | TotalMonthEnergy（LSW） | u16 | 1 | kWh
0x0305 | RO | TotalMonthEnergy（MSW） | u16 | 1 | kWh
0x0306 | RO | TotalDateEnergy | u16 | 1 | kWh
0x0307 | RO | TotalHourEnergy_0 | u16 | 1 | kWh
0x0308 | RO | TotalHourEnergy_1 | u16 | 1 | kWh
0x0309 | RO | TotalHourEnergy_2 | u16 | 1 | kWh
0x030A | RO | TotalHourEnergy_3 | u16 | 1 | kWh
0x030B | RO | TotalHourEnergy_4 | u16 | 1 | kWh
0x030C | RO | TotalHourEnergy_5 | u16 | 1 | kWh
0x030D | RO | TotalHourEnergy_6 | u16 | 1 | kWh
0x030E | RO | TotalHourEnergy_7 | u16 | 1 | kWh
0x030F | RO | TotalHourEnergy_8 | u16 | 1 | kWh
0x0310 | RO | TotalHourEnergy_9 | u16 | 1 | kWh
0x0311 | RO | TotalHourEnergy_10 | u16 | 1 | kWh
0x0312 | RO | TotalHourEnergy_11 | u16 | 1 | kWh
0x0313 | RO | TotalHourEnergy_12 | u16 | 1 | kWh
0x0314 | RO | TotalHourEnergy_13 | u16 | 1 | kWh
0x0315 | RO | TotalHourEnergy_14 | u16 | 1 | kWh
0x0316 | RO | TotalHourEnergy_15 | u16 | 1 | kWh
0x0317 | RO | TotalHourEnergy_16 | u16 | 1 | kWh
0x0318 | RO | TotalHourEnergy_17 | u16 | 1 | kWh
0x0319 | RO | TotalHourEnergy_18 | u16 | 1 | kWh
0x031A | RO | TotalHourEnergy_19 | u16 | 1 | kWh
0x031B | RO | TotalHourEnergy_20 | u16 | 1 | kWh
0x031C | RO | TotalHourEnergy_21 | u16 | 1 | kWh
0x031D | RO | TotalHourEnergy_22 | u16 | 1 | kWh
0x031E | RO | TotalHourEnergy_23 | u16 | 1 | kWh
0x0500 | RW | Work state control command | u16 | N/A | N/A | Bit2:Stop |  | UC
Bit5:Standby
Bit6:Run
0x0501 | RW | Active power command | i16 | 0.1 | kW |  | postive:discharge negative:charge
0x0502 | RW | Reactive power command | i16 | 0.1 | kvar |  | postive:provides reactive negative:absorbs reactive
0x0503 | RW | PV PowerLimit command | u16 | 0.1 | kW | 0~600
0x0601 | RW | Work mode control command | u16 | N/A | N/A | Bit9：P/Q（Remote dispatch） |  | UC
0xA000 | RO | DCDC work state | u16 | N/A | N/A | Bit0:Reserved |  | DCDC
Bit1:Initial
Bit2:Stop
Bit3:Ready
Bit4:Running
Bit5:Fault
Bit6:Debug
Bit7:Locked
0xA001 | RO | DCDC work mode | u16 | N/A | N/A | Bit0:Reserved
Bit1:Reserved
Bit2:Reserved
Bit3:Reserved
Bit4:Reserved
Bit5:Reserved
Bit6:Reserved
Bit7:const.current
Bit8:const.volt.
Bit9:BOOST MPPT
0xA100 | RO | Suggestive information(DCDC) | u16 | N/A | N/A | Bit0:Current sampling channel abnormity on high voltage side | 1:appear; 0:disappear | DCDC
Bit1:Current sampling channel abnormity on low voltage side
Bit2:Reserved
Bit3:Reserved
Bit4:Reserved
Bit5:Reserved
Bit6:EEPROM parameters over range
Bit7:Update EEPROM failed
Bit8:Read EEPROM failed
Bit9:Current sampling channel abnormity before inductance
Bit10~Bit15:Reserved
0xA101 | RO | Suggestive information(DCDC) | u16 | N/A | N/A | Bit0:Reactor power decrease caused by overtemperature | 1:appear; 0:disappear
Bit1:IGBT power decrease caused by overtemperature
Bit2:Temperature chanel3 power decrease caused by overtemperature
Bit3:Temperature chanel4 power decrease caused by overtemperature
Bit4:Temperature chanel5 power decrease caused by overtemperature
Bit5:Temperature chanel6 power decrease caused by overtemperature
Bit6:Temperature chanel7 power decrease caused by overtemperature
Bit7:Temperature chanel8 power decrease caused by overtemperature
Bit8:Fan 1 stop failed
Bit9:Fan 2 stop failed
Bit10:Fan 3 stop failed
Bit11:Fan 4 stop failed
Bit12:Fan 1 sartup failed
Bit13:Fan 2 sartup failed
Bit14:Fan 3 sartup failed
Bit15:Fan 4 sartup failed
0xA102 | RO | Suggestive information(DCDC) | u16 | N/A | N/A | Bit0：High voltage side overvoltage | 1:appear; 0:disappear
Bit1：High voltage side undervoltage
Bit2：High voltage side voltage change unconventionally
Bit3-Bit15：Reserved
0xA103 | RO | Suggestive information(DCDC) | u16 | N/A | N/A | Bit0：Current abnormity before DC Converter work on high voltage side | 1:appear; 0:disappear
Bit1：Current abnormity before DC Converter work on low voltage side
Bit2：Initial Duty Ratio abnormity before DC Converter work
Bit3：Voltage abnormity before DC Converter work on high voltage side
Bit4：Voltage abnormity before DC Converter work on low voltage side
Bit5-Bit15：Reserved
0xA104 | RO | Suggestive information(DCDC) | u16 | N/A | N/A | Bit0：High voltage breaker inspection abnormity | 1:appear; 0:disappear
Bit1：Low voltage breaker inspection abnormity
Bit2：DC precharge contactor inspection abnormity
Bit3：DC precharge contactor open unsuccessfully
Bit2：DC main contactor inspection abnormity
Bit5：DC main contactor open unsuccessfully
Bit6：Output contactor close unsuccessfully
Bit7：Output contactor open unsuccessfully
Bit8：AC main contactor close unsuccessfully
Bit9：AC main contactor open unsuccessfully
Bit10：NegContactor open unsuccessfully
Bit11：NegContactor close unsuccessfully
Bit12：NegContactor state abnormal
Bit13-Bit15：Reserved
0xA110 | RO | Abnormity(DCDC) | u16 | N/A | N/A | Bit0：High voltage side of DC Converter undervoltage | 1:appear; 0:disappear | DCDC
Bit1：High voltage side of DC Converter overvoltage
Bit2：Low voltage side of DC Converter undervoltage
Bit3：Low voltage side of DC Converter overvoltage
Bit4：High voltage side of DC Converter overcurrent fault
Bit5：Low voltage side of DC Converter overcurrent fault
Bit6：DC Converter IGBT fault
Bit7：DC Converter Precharge unmet
Bit8-Bit15：Reserved
0xA111 | RO | Abnormity(DCDC) | u16 | N/A | N/A | Bit0：BECU communication disconnected | 1:appear; 0:disappear
Bit1：DC Converter communication disconnected
Bit2：Current configuration over range
Bit3：The battery request stop
Bit4：Reserved
Bit5：Overcurrent relay fault
Bit6：Lightning protection device fault
Bit7：DC Converter priamary contactor disconnected abnormally
Bit8：Reserved
Bit9：DC disconnected abnormally on low voltage side of DC convetor
Bit10：Reserved
Bit11：Reserved
Bit12：DC convetor EEPROM abnormity 1
Bit13：DC convetor EEPROM abnormity 1
Bit14：EDC convetor EEPROM abnormity 1
Bit15：Reserved
0xA112 | RO | Abnormity(DCDC) | u16 | N/A | N/A | Bit0：DC Convertor general overload | 1:appear; 0:disappear
Bit1：DC short circuit
Bit2：Peak pulse current protection
Bit3：DC disconnect abnormally on high voltage side of DC convetor
Bit4：Effective pulse value overhigh
Bit5：DC Converte severe overload
Bit6：DC breaker disconnect abnormally on high voltage side of DC convetor
Bit7：DC breaker disconnect abnormally on low voltage side of DC convetor
Bit8：DC convetor precharge contactor close failed
Bit9：DC convetor main contactor close failed
Bit10：AC contactor state abnormity of DC convetor
Bit11：DC convetor emergency stop
Bit12：DC converter charging gun disconnected
Bit13：DC current abnormity before DC convetor work
Bit14：Fuse disconnected
Bit15：DC converter hardware current or voltage fault
0xA113 | RO | Abnormity(DCDC) | u16 | N/A | N/A | Bit0：DC converter crystal oscillator circuit invalidation | 1:appear; 0:disappear
Bit1：DC converter reset circuit invalidation
Bit2：DC converter sampling circuit invalidation
Bit3：DC converter digital I/O circuit invalidation
Bit4：DC converter PWM circuit invalidation
Bit5：DC converter X5045 circuit invalidation
Bit6：DC converter CAN circuit invalidation
Bit7：DC converter software&hardware protection circuit invalidation
Bit8：DC converter power circuit invalidation
Bit9：DC converter CPU invalidation
Bit10：DC converter TINT0 interrupt invalidation
Bit11：DC converter ADC interrupt invalidation
Bit12：DC converter CAPITN4 interrupt invalidation
Bit13：DC converter CAPINT6 interrupt invalidation
Bit14：DC converter T3PINTinterrupt invalidation
Bit15：DC converter T4PINTinterrupt invalidation
0xA114 | RO | Abnormity(DCDC) | u16 | N/A | N/A | Bit0：DC converter PDPINTA interrupt invalidation | 1:appear; 0:disappear
Bit1：DC converter T1PINT interrupt invalidation
Bit2：DC converter RESV interrupt invalidation
Bit3：DC converter 100us task invalidation
Bit4：DC converter clock invalidation
Bit5：DC converter EMS memory invalidation
Bit6：DC converter exterior communication invalidation
Bit7：DC converter IO Interface invalidation
Bit8：DC converter Input Voltage bound fault
Bit9：DC converter Outter Voltage bound fault
Bit10：DC converter Output Voltage bound fault
Bit11：DC converter Induct Current bound fault
Bit12：DC converter Input Current bound fault
Bit13：DC converter Output Current bound fault
Bit14-Bit15：Reserved
0xA115 | RO | Abnormity(DCDC) | u16 | N/A | N/A | Bit0：DC Reactor over temperature | 1:appear; 0:disappear
Bit1：DC IGBT over temperature
Bit2：DC Converter chanel 3 over temperature
Bit3：DC Converter chanel 4 over temperature
Bit4：DC Converter chanel 5 over temperature
Bit5：DC Converter chanel 6 over temperature
Bit6：DC Converter chanel 7 over temperature
Bit7：DC Converter chanel 8 over temperature
Bit8：DC Reactor temperature sampling invalidation
Bit9：DC IGBT temperature sampling invalidation
Bit10：DC Converter chanel 3 temperature sampling invalidation
Bit11：DC Converter chanel 4 temperature sampling invalidation
Bit12：DC Converter chanel 5 temperature sampling invalidation
Bit13：DC Converter chanel 6 temperature sampling invalidation
Bit14：DC Converter chanel 7 temperature sampling invalidation
Bit15：DC Converter chanel 8 temperature sampling invalidation
0xA116 | RO | Abnormity(DCDC) | u16 | N/A | N/A | Bit0-Bit4：Reserved | 1:appear; 0:disappear
Bit5：DC Converter inductance current sampling invalidation
Bit6：Current sampling invalidation on the low voltage sideof DC Converter
Bit7：Voltage sampling invalidation on the low voltage side of DC Converter
Bit8：Insulation inspection fault
Bit9：NegContactor close unsuccessly
Bit10：NegContactor cut When running
Bit11-Bit15：Reserved
0xA120 | RO | Switch state(DCDC) | u16 | N/A | N/A | Bit0:DC precharge contactor | 0:OFF 1:ON | DCDC
Bit1:DC main contactor
Bit2: Output contactor
Bit3:Output breaker
Bit4:Input breaker
Bit5:AC contactor
Bit6:Emergency stop button
Bit7:NegContactor
Bit8-Bit15:Reserved
0xA130 | RO | Output voltage(DCDC) | i16 | 0.1 | V |  |  | DCDC
0xA131 | RO | Output current(DCDC) | i16 | 0.1 | A
0xA132 | RO | Output power(DCDC) | i16 | 0.1 | kW
0xA133 | RO | Intput voltage(DCDC) | i16 | 0.1 | V
0xA134 | RO | Intput current(DCDC) | i16 | 0.1 | A
0xA135 | RO | Intput power(DCDC) | i16 | 0.1 | kW
0xA136 | RO | Input Engergy(DCDC) | i16 | 0.1 | kWh
0xA137 | RO | Output Engergy(DCDC) | i16 | 0.1 | kWh
0xA140 | RO | Reactor temperature(DCDC) | i16 | 1 | ℃ |  |  | DCDC
0xA141 | RO | IGBT temperature(DCDC) | i16 | 1 | ℃
0xA150 | RO | Input Total Charge Energy(LSW) | u16 | 0.1 | kWh | Total = (MSW << 16 ¦ LSW) |  | DCDC
0xA151 | RO | Input Total Charge Energy(MSW) | u16
0xA152 | RO | Input Total DisCharge Energy(LSW) | u16 | 0.1 | kWh | Total = (MSW << 16 ¦ LSW)
0xA153 | RO | Input Total DisCharge Energy(MSW) | u16
0xA154 | RO | Output Total Charge Energy(LSW) | u16 | 0.1 | kWh | Total = (MSW << 16 ¦ LSW)
0xA155 | RO | Output Total Charge Energy(MSW) | u16
0xA156 | RO | Output Total DisCharge Energy(LSW) | u16 | 0.1 | kWh | Total = (MSW << 16 ¦ LSW)
0xA157 | RO | Output Total DisCharge Energy(MSW) | u16
The information of BMS DCDC（BMS DCDC1 、PV DCDC and PV DCDC1） is the same as 0xA000-0xA202，the offset is0x300；For example，the work state of BMS DCDC1：0xA300；the work state of PV DCDC：0xA600；the work state of PV DCDC1：0xA900；

## BMS
Register Address（HEX） | Data Type | Data Meaning | Value Type | Coefficient | Unit | Remark | Note
0x1100 | RO | Battery string work state | u16 | N/A | N/A | Bit0:Initial
Bit1:Stop
Bit2:Starting up
Bit3:Running
Bit4:Fault
0x1101 | RO | Battery string switch state | u16 | N/A | N/A | bit0:Main contactor | 1:closed ；0:open
bit1:Precharge contactor
bit2:FAN contactor
bit3:BMU power supply relay
bit4:Middle relay
Bit5-bit15:Reserved
0x1102 | RO | Battery string peripheral IO state | u16 | N/A | N/A | bit0:Fuse state | 1:closed ；0:open
bit4:iIsolated switch state
bit5-bit15:Reserved
0x1103 | RO | Battery string suggestive information | u16 | N/A | N/A | Bit0:Battery string charge general overcurrent | 1:appear 0:disappear
Bit1:Battery string discharge general overcurrent
Bit2:Battery string charge current over limit
Bit3:Battery string discharge current over limit
Bit4:Battery string general overvoltage
Bit5:Battery string general undervoltage
Bit6:Reserved
Bit7:Battery string general over temperature
Bit8:Battery string general under temperature
Bit9:Reserved
Bit10:Battery string severe overvoltage
Bit11:Battery string severe under voltage
Bit12:Battery string severe under temperature
Bit13:Battery string charge severe overcurrent
Bit14:Battery string discharge severe overcurrent
Bit15:Battery string capacity abnormity
0x1105 | RO | Battery string abnormity | u16 | N/A | N/A | Bit0:Reserved | 1:appear 0:disappear
Bit1:Reserved
Bit2:Battery string voltage sampling route invalidation
Bit3:Reserved
Bit4:Battery string voltage sampling route disconnected
Bit5:Battery string temperature sampling route disconnected
Bit6:Battery string inside CAN disconnected
Bit7:Reserved
Bit8:Reserved
Bit9:Battery string current sampling circuit abnormity
Bit10:Battery string battery cell invalidation
Bit11:Battery string main contactor inspection abnormity
Bit12:Battery string precharge contactor inspection abnormity
Bit13:Battery string negative contactor inspection abnormity
Bit14:Battery string power supply relay inspection abnormity
Bit15:Battery string middle relay abnormity
0x1106 | RO | Battery string abnormity | u16 | N/A | N/A | Bit0:Reserved | 1:appear 0:disappear
Bit1:Reserved
Bit2:Battery string severe overtemperature
Bit3:Reserved
Bit4:Reserved
Bit5:Reserved
Bit6:Reserved
Bit7:Battery string smog fault
Bit8:Battery string blown fuse indicator fault
Bit9:Reserved
Bit10:Battery string general leakage
Bit11:Battery string severe leakage
Bit12:Communication between BECU and periphery CAN disconnected
Bit13:Reserved
Bit14:Battery string power supply relay contactor disconnected
Bit15:Reserved
0x1400 | RO | Battery string total voltage | u16 | 0.1 | V
0x1401 | RO | Battery string total current | i16 | 0.1 | A
0x1402 | RO | Battery string SOC | u16 | 1 | %
0x1403 | RO | Battery string SOH | u16 | 1 | %
0x1404 | RO | Battery string cell average temperature | i16 | 1 | ℃
0x1406 | RO | Battery string charge current limit | u16 | 0.1 | A
0x1407 | RO | Battery string discharge current limit | u16 | 0.1 | A
0x140A | RO | Battery string charge/discharge times（LSW） | u16 | 1 | N/A
0x140B | RO | Battery string charge/discharge times（MSW） | u16 | 1 | N/A
0x1418 | RO | Battery string accumulated charge energy（LSW） | u16 | 1 | Wh
0x1419 | RO | Battery string accumulated charge energy（MSW） | u16 | 1 | Wh
0x141A | RO | Battery string accumulated discharge energy（LSW） | u16 | 1 | Wh
0x141B | RO | Battery string accumulated discharge energy（MSW） | u16 | 1 | Wh
0x1420 | RO | Battery Power | i16 | 0.1 | kW | Battery output power
0x1430 | RO | Battery string Max cell voltage battery NO. | u16 | 1 | N/A
0x1431 | RO | Battery string Max cell voltage | u16 | 0.001 | V
0x1432 | RO | Temperature of Battery string Max voltage cell | i16 | 1 | ℃
0x1433 | RO | Battery string Min cell voltage battery NO. | u16 | 1 | N/A
0x1434 | RO | Battery string Min cell voltage | u16 | 0.001 | V
0x1435 | RO | Temperature of Battery string Min voltage cell | i16 | 1 | ℃
0x143A | RO | Battery string Max cell temperature battery NO. | u16 | 1 | N/A
0x143B | RO | Battery string Max cell temperature | i16 | 1 | ℃
0x143C | RO | Voltage of Battery string Max temperature cell | u16 | 0.001 | V
0x143D | RO | Battery string Min cell temperature battery NO. | u16 | 1 | N/A
0x143E | RO | Battery string Min cell temperature | i16 | 1 | ℃
0x143F | RO | Voltage of Battery string Min temperature cell | u16 | 0.001 | V
0x1500~0x16FF | RO | Battery string cell voltage | u16 | 0.001 | V | 1~64
0x1700~0x18FF | RO | Battery string cell temperature | i16 | 1 | ℃ | 1~64

## log
N0. | Description | Ver. | Modifier | Date
1 | First release of Modbus Register List | V001.00 | Mamingjun
2 | Add total energy | V001.01 | Mamingjun
3 | Add PV total output energy | V001.02 | Mamingjun
4 | Add DCDC suggestive | V001.03 | Yangrongchun
5 | Modify DCDC total energy registers | V001.04 | Mamingjun
6 | Add load shifting mode control registers | V001.05 | Mamingjun
7 | Add CMLO/GMLP mode control registers | V001.06 | Mamingjun
8 | Modify Unit work state,add PCS work state | V001.07 | Mamingjun
9 | Add capacity test mode control registers | V001.08 | Yangrongchun
10 | Add diesel mode and parameters | V001.09 | Yangrongchun
11 | Add battery output power and Unit ON/OFF Grid state registers | V001.10 | Yangrongchun
12 | Modify PCS and BMS suggestive&abnormity information | V001.11 | Mamingjun
13 | Add output power control command registers | V001.12 | Mamingjun
14 | Delete DCDC information for AC system | V001.13 | Mamingjun
15 | Add allowable charging/discharging power,protocol version,producer and system style registers | V001.14 | Mamingjun
16 | Add PV powerLimit command | V001.15 | Mamingjun
17 | Add DCDC information for DC system | V001.16 | Qinxiqun | 2016-01-26
18 | Modify PV powerLimit command | v001.17 | Liutongxin | 2016-03-25
19 | Modify DCDC abnormity information，add standby control command | V001.18 | Qinxiqun | 2016-04-29
20 | Add Inverter info. | V001.19 | Qinxiqun | 2016-06-08