## License Agreement
SunSpec Alliance
SunSpec Infomation Model Reference
Date Generated: 2016-04-20
This document is generated programatically from the canonical model definitions contained in the SunSpec model repository.
For the most up-to-date version of this document, go to: www.sunspec.org/download
Copyright SunSpec Alliance 2009-2015. All Rights Reserved.
This document and the information contained herein is provided on an "AS IS" basis and the SunSpec Alliance DISCLAIMS ALL WARRANTIES, EXPRESS OR IMPLIED, INCLUDING BUT NOT LIMITED TO ANY WARRANTY THAT THE USE OF THE INFORMATION HEREIN WILL NOT INFRINGE ANY OWNERSHIP RIGHTS OR ANY IMPLIED WARRANTIES OF MERCHANTABILITY OR FITNESS FOR A PARTICULAR PURPOSE.
This document may be used, copied, and furnished to others, without restrictions of any kind, provided that this document itself may not be modified in anyway, except as needed by the SunSpec Technical Committee and as governed by the SunSpec IPR Policy. The complete policy of the SunSpec Alliance can be found at www.sunspec.org.
Prepared by the SunSpec Alliance
4030 Moorpark Avenue, Suite 109
San Jose, CA 95117
Website: www.sunspec.org
Email: info@sunspec.org

## Summary
Summary
This spreadsheet describes SunSpec Alliance Data Models and Modbus maps.
Each spreadsheet tab describes an individual data model of one of the following types:
Id Range | Model Type
1 | Common
2 | Aggregator
010 to 019 | Network Configuration
100 series | Inverter
200 series | Meter
300 series | Environmental
400 series | String Combiner
500 series | Panel
600 series | Tracker
700 series | Reserved by SunSpec Alliance
800 series | Storage
900 - 63000 | Reserved by SunSpec Alliance
64000 series | Vendor Specific
This document includes data models that are of Approved, Test, and Draft status.
Before using any of these models, please check the release status of the model in question.
Only Approved models may be SunSpec Certified.
Canonical Representation
The documentation contained in this spreadsheet is derived from SunSpec Model Definition XML (SMDX) files, which can be downloaded from www.sunspec.org/modelreference/
Please note that the SMDX files are the canonical (definitive) representations of SunSpec models.
SunSpec Specification Documentation
All current SunSpec specifications (PDF format) are available for free downloading at http://sunspec.org/download/.
SunSpec Certification
If you would like to have your product SunSpec Certified, please read the information available at http://sunspec.org/sunspec-certified-program/
and then email certification@sunspec.org to schedule your test.

## Index
Model | Label | Description | Notes
1 | Common | All SunSpec compliant devices must include this as the first model
2 | Basic Aggregator | Aggregates a collection of models for a given model id
3 | Secure Dataset Read Request | Request a digial signature over a specifed set of data registers | Used in conjunction witgh Secure Dataset Read Response Model
4 | Secure Dataset Read Response | Compute a digial signature over a specifed set of data registers
5 | Secure Write Request | Include a digial signature along with the control data
6 | Secure Write Sequential Request | Include a digial signature along with the control data
7 | Secure Write Response Model (DRAFT 1) | Include a digital signature over the response | Used in conjunction with a Secure Write Request
8 | Get Device Security Certificate | Security model for PKI
9 | Set Operator Security Certificate | Security model for PKI
10 | Communication Interface Header | To be included first for a complete interface description
11 | Ethernet Link Layer | Include to support a wired ethernet port
12 | IPv4 | Include to support an IPv4 protocol stack on this interface
13 | IPv6 | Include to support an IPv6 protocol stack on this interface
14 | Proxy Server | Include this block to allow for a proxy server
15 | Interface Counters Model | Interface counters
16 | Simple IP Network | Include this model for a simple IPv4 network stack
17 | Serial Interface | Include this model for serial interface configuration support
18 | Cellular Link | Include this model to support a cellular interface link
19 | PPP Link | Include this model to configure a Point-to-Point Protocol link
101 | Inverter (Single Phase) | Include this model for single phase inverter monitoring
102 | Inverter (Split-Phase) | Include this model for split phase inverter monitoring
103 | Inverter (Three Phase) | Include this model for three phase inverter monitoring
111 | Inverter (Single Phase) FLOAT | Include this model for single phase inverter monitoring using float values
112 | Inverter (Split Phase) FLOAT | Include this model for split phase inverter monitoring using float values
113 | Inverter (Three Phase) FLOAT | Include this model for three phase inverter monitoring using float values
120 | Nameplate | Inverter Controls Nameplate Ratings | Ref 3: 8.14.3.2, Ref 4: 17
121 | Basic Settings | Inverter Controls Basic Settings | Ref 3: 8.4.2.1, Ref 4: 17
122 | Measurements_Status | Inverter Controls Extended Measurements and Status | Ref 3: 8.14.3.2, Ref 4: 17
123 | Immediate Controls | Immediate Inverter Controls | Ref 3: 8.7.1.2, 8.7.2.2, 8.7.3.2
124 | Storage | Basic Storage Controls | Ref 3: 8.7.4.2
125 | Pricing | Pricing Signal | Ref 3: 8.7.5.1; Ref 4: 6
126 | Static Volt-VAR | Static Volt-VAR Arrays | Ref 3: 8.8.1.2
127 | Freq-Watt Param | Parameterized Frequency-Watt | Ref 3: 8.9.1.2, 8.9.4.2
128 | Dynamic Reactive Current | Dynamic Reactive Current | Ref 3: 8.10.1.2; Ref 4: 12
129 | LVRTD | LVRT Must Disconnect | Ref 4: 11
130 | HVRTD | HVRT Must Disconnect | Ref 4: 11
131 | Watt-PF | Watt-Power Factor | Ref 3: 8.11.1.2
132 | Volt-Watt | Volt-Watt | Ref 3: 8.12.1.2
133 | Basic Scheduling | Basic Scheduling | Ref 2: 2.2.8
134 | Freq-Watt Crv | Curve-Based Frequency-Watt | Ref 3: 8.9.1.2, 8.9.4.2
135 | LFRT | Low Frequency Ride-through | Ref 4: 11
136 | HFRT | High Frequency Ride-through | Ref 4: 11
137 | LVRTC | LVRT must remain connected | Ref 4: 11
138 | HVRTC | HVRT must remain connected | Ref 4: 11
160 | Multiple MPPT Inverter Extension Model
201 | Meter (Single Phase)single phase (AN or AB) meter | Include this model for single phase (AN or AB) metering
202 | split single phase (ABN) meter
203 | wye-connect three phase (abcn) meter
204 | delta-connect three phase (abc) meter
211 | single phase (AN or AB) meter |  | Float
212 | split single phase (ABN) meter |  | Float
213 | wye-connect three phase (abcn) meter |  | Float
214 | delta-connect three phase (abc) meter |  | Float
220 | Secure AC Meter Selected Readings | Include this model for secure metering
302 | Irradiance Model | Include to support various irradiance measurements
303 | Back of Module Temperature Model | Include to support variable number of back of module temperature measurements
304 | Inclinometer Model | Include to support orienation measurements
305 | GPS | Include to support location measurements
306 | Reference Point Model | Include to support a standard reference point
307 | Base Met | Base Meteorolgical Model | This model supersedes model 301
308 | Mini Met Model | Include to support a few basic measurements
401 | String Combiner (Current) | A basic string combiner | This model is SUPERSEDED by model 403
402 | String Combiner (Advanced) | An advanced string combiner | This model is SUPERSEDED by model 404
403 | String Combiner (Current) | A basic string combiner model | This model supersedes model 401
404 | String Combiner (Advanced) | An advanced string combiner including voltage and energy measurements | This model supersedes model 402
501 | Solar Module | A solar module model supporing DC-DC converter | Float
502 | Solar Module | A solar module model supporing DC-DC converter | Integer
601 | Tracker Controller DRAFT 2 | Monitors and controls multiple trackers | Trackers may include GPS model 305 for location information
801 | Energy Storage Base Model
802 | Battery Base Model
803 | Lithium-Ion Battery Model
63001 | SunSpec Test Model 1
63002 | SunSpec Test Model 2
64001 | Veris Status and Configuration
64020 | Mersen GreenString
64101 | Eltek Inverter Extension
64110 | OutBack AXS device
64111 | Basic Charge Controller
64112 | OutBack FM Charge Controller
SunSpec Model is unsupported / Element of SunSpec model is NOT implemented
SunSpec Model is supported / Element of SunSpec model is implemented
Element of SunSpec model is implemented, but may not be written periodically
Element of SunSpec model is implemented only for special inverter models/configurations

## 1
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Common | 1 | uint16 |  |  | R | M | All SunSpec compliant devices must include this as the first model
Header |  | 1 |  | 1 | L |  | 66 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 16 | Mn | Manufacturer |  | string |  |  | R | M | Well known value registered with SunSpec for compliance
Fixed Block |  | 18 | 16 | 16 | Md | Model |  | string |  |  | R | M | Manufacturer specific value (32 chars)
Fixed Block |  | 34 | 32 | 8 | Opt | Options |  | string |  |  | R | O | Manufacturer specific value (16 chars)
Fixed Block |  | 42 | 40 | 8 | Vr | Version |  | string |  |  | R | O | Manufacturer specific value (16 chars)
Fixed Block |  | 50 | 48 | 16 | SN | Serial Number |  | string |  |  | R | M | Manufacturer specific value (32 chars)
Fixed Block |  | 66 | 64 | 1 | DA | Device Address |  | uint16 |  |  | RW | O | Modbus device address
Fixed Block |  | 67 | 65 | Size: 1; Name: Pad; Type: pad; R/W: R | O | Force even alignment

## 2
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Basic Aggregator | 2 | uint16 |  |  | R | M | Aggregates a collection of models for a given model id
Header |  | 1 |  | 1 | L |  | 14 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | AID | AID |  | uint16 |  |  | R | M | Aggregated model id
Fixed Block |  | 3 | 1 | 1 | N | N |  | uint16 |  |  | R | M | Number of aggregated models
Fixed Block |  | 4 | 2 | 1 | UN | UN |  | uint16 |  |  | R | M | Update Number. Incrementing nunber each time the mappping is changed. If the number is not changed from thelast reading the direct access to a specific offset will result in reading the same logical model as before. Otherwise the entire model must be read to refresh the changes
Fixed Block |  | 5 | 3 | 1 | St | Status |  | enum16 |  |  | R | M | Enumerated status code
Fixed Block |  | 6 | 4 | 1 | StVnd | Vendor Status |  | enum16 |  |  | R | O | Vendor specific status code
Fixed Block |  | 7 | 5 | 2 | Evt | Event Code |  | bitfield32 |  |  | R | M | Bitmask event code
Fixed Block |  | 9 | 7 | 2 | EvtVnd | Vendor Event Code |  | bitfield32 |  |  | R | O | Vendor specific event code
Fixed Block |  | 11 | 9 | 1 | Ctl | Control |  | enum16 |  |  | R | O | Control register for all aggregated devices
Fixed Block |  | 12 | 10 | 2 | CtlVnd | Vendor Control |  | enum32 |  |  | R | O | Vendor control register for all aggregated devices
Fixed Block |  | 14 | 12 | 2 | CtlVl | Control Value |  | enum32 |  |  | R | O | Numerical value used as a parameter to the control
enum16 | St |  |  | Name: OFF; Value: 1
enum16 | St |  |  | Name: ON; Value: 2
enum16 | St |  |  | Name: FULL; Value: 3
enum16 | St |  |  | Name: FAULT; Value: 4
bitfield32 | Evt |  |  | Name: GROUND_FAULT; Value: 0
bitfield32 | Evt |  |  | Name: INPUT_OVER_VOLTAGE; Value: 1
bitfield32 | Evt |  |  | Name: RESERVED; Value: 11
bitfield32 | Evt |  |  | Name: DC_DISCONNECT; Value: 3
bitfield32 | Evt |  |  | Name: MANUAL_SHUTDOWN; Value: 6
bitfield32 | Evt |  |  | Name: OVER_TEMPERATURE; Value: 7
bitfield32 | Evt |  |  | Name: BLOWN_FUSE; Value: 12
bitfield32 | Evt |  |  | Name: UNDER_TEMPERATURE; Value: 13
bitfield32 | Evt |  |  | Name: MEMORY_LOSS; Value: 14
bitfield32 | Evt |  |  | Name: ARC_DETECTION; Value: 15
bitfield32 | Evt |  |  | Name: THEFT_DETECTION; Value: 16
bitfield32 | Evt |  |  | Name: OUTPUT_OVER_CURRENT; Value: 17
bitfield32 | Evt |  |  | Name: OUTPUT_OVER_VOLTAGE; Value: 18
bitfield32 | Evt |  |  | Name: OUTPUT_UNDER_VOLTAGE; Value: 19
bitfield32 | Evt |  |  | Name: TEST_FAILED; Value: 20
enum16 | Ctl |  |  | Name: NONE; Value: 0
enum16 | Ctl |  |  | Name: AUTOMATIC; Value: 1
enum16 | Ctl |  |  | Name: FORCE_OFF; Value: 2
enum16 | Ctl |  |  | Name: TEST; Value: 3
enum16 | Ctl |  |  | Name: THROTTLE; Value: 4

## 3
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Secure Dataset Read Request | 3 | uint16 |  |  | R | M | Request a digial signature over a specifed set of data registers | Used in conjunction witgh Secure Dataset Read Response Model
Header |  | 1 |  | 1 | L |  | 58 + (RB Count * 1) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | X | X |  | uint16 |  |  | RW | M | Number of registers being requested | A max of 50 registers are allowed
Fixed Block |  | 3 | 1 | 1 | Off1 | Offset1 |  | uint16 |  |  | RW | M | Offset of value to read
Fixed Block |  | 4 | 2 | Size: 1; Name: Off2; Type: uint16; R/W: RW | M
Fixed Block |  | 5 | 3 | Size: 1; Name: Off3; Type: uint16; R/W: RW | M
Fixed Block |  | 6 | 4 | Size: 1; Name: Off4; Type: uint16; R/W: RW | M
Fixed Block |  | 7 | 5 | Size: 1; Name: Off5; Type: uint16; R/W: RW | M
Fixed Block |  | 8 | 6 | Size: 1; Name: Off6; Type: uint16; R/W: RW | M
Fixed Block |  | 9 | 7 | Size: 1; Name: Off7; Type: uint16; R/W: RW | M
Fixed Block |  | 10 | 8 | Size: 1; Name: Off8; Type: uint16; R/W: RW | M
Fixed Block |  | 11 | 9 | Size: 1; Name: Off9; Type: uint16; R/W: RW | M
Fixed Block |  | 12 | 10 | Size: 1; Name: Off10; Type: uint16; R/W: RW | M
Fixed Block |  | 13 | 11 | Size: 1; Name: Off11; Type: uint16; R/W: RW | M
Fixed Block |  | 14 | 12 | Size: 1; Name: Off12; Type: uint16; R/W: RW | M
Fixed Block |  | 15 | 13 | Size: 1; Name: Off13; Type: uint16; R/W: RW | M
Fixed Block |  | 16 | 14 | Size: 1; Name: Off14; Type: uint16; R/W: RW | M
Fixed Block |  | 17 | 15 | Size: 1; Name: Off15; Type: uint16; R/W: RW | M
Fixed Block |  | 18 | 16 | Size: 1; Name: Off16; Type: uint16; R/W: RW | M
Fixed Block |  | 19 | 17 | Size: 1; Name: Off17; Type: uint16; R/W: RW | M
Fixed Block |  | 20 | 18 | Size: 1; Name: Off18; Type: uint16; R/W: RW | M
Fixed Block |  | 21 | 19 | Size: 1; Name: Off19; Type: uint16; R/W: RW | M
Fixed Block |  | 22 | 20 | Size: 1; Name: Off20; Type: uint16; R/W: RW | M
Fixed Block |  | 23 | 21 | Size: 1; Name: Off21; Type: uint16; R/W: RW | M
Fixed Block |  | 24 | 22 | Size: 1; Name: Off22; Type: uint16; R/W: RW | M
Fixed Block |  | 25 | 23 | Size: 1; Name: Off23; Type: uint16; R/W: RW | M
Fixed Block |  | 26 | 24 | Size: 1; Name: Off24; Type: uint16; R/W: RW | M
Fixed Block |  | 27 | 25 | Size: 1; Name: Off25; Type: uint16; R/W: RW | M
Fixed Block |  | 28 | 26 | Size: 1; Name: Off26; Type: uint16; R/W: RW | M
Fixed Block |  | 29 | 27 | Size: 1; Name: Off27; Type: uint16; R/W: RW | M
Fixed Block |  | 30 | 28 | Size: 1; Name: Off28; Type: uint16; R/W: RW | M
Fixed Block |  | 31 | 29 | Size: 1; Name: Off29; Type: uint16; R/W: RW | M
Fixed Block |  | 32 | 30 | Size: 1; Name: Off30; Type: uint16; R/W: RW | M
Fixed Block |  | 33 | 31 | Size: 1; Name: Off31; Type: uint16; R/W: RW | M
Fixed Block |  | 34 | 32 | Size: 1; Name: Off32; Type: uint16; R/W: RW | M
Fixed Block |  | 35 | 33 | Size: 1; Name: Off33; Type: uint16; R/W: RW | M
Fixed Block |  | 36 | 34 | Size: 1; Name: Off34; Type: uint16; R/W: RW | M
Fixed Block |  | 37 | 35 | Size: 1; Name: Off35; Type: uint16; R/W: RW | M
Fixed Block |  | 38 | 36 | Size: 1; Name: Off36; Type: uint16; R/W: RW | M
Fixed Block |  | 39 | 37 | Size: 1; Name: Off37; Type: uint16; R/W: RW | M
Fixed Block |  | 40 | 38 | Size: 1; Name: Off38; Type: uint16; R/W: RW | M
Fixed Block |  | 41 | 39 | Size: 1; Name: Off39; Type: uint16; R/W: RW | M
Fixed Block |  | 42 | 40 | Size: 1; Name: Off40; Type: uint16; R/W: RW | M
Fixed Block |  | 43 | 41 | Size: 1; Name: Off41; Type: uint16; R/W: RW | M
Fixed Block |  | 44 | 42 | Size: 1; Name: Off42; Type: uint16; R/W: RW | M
Fixed Block |  | 45 | 43 | Size: 1; Name: Off43; Type: uint16; R/W: RW | M
Fixed Block |  | 46 | 44 | Size: 1; Name: Off44; Type: uint16; R/W: RW | M
Fixed Block |  | 47 | 45 | Size: 1; Name: Off45; Type: uint16; R/W: RW | M
Fixed Block |  | 48 | 46 | Size: 1; Name: Off46; Type: uint16; R/W: RW | M
Fixed Block |  | 49 | 47 | Size: 1; Name: Off47; Type: uint16; R/W: RW | M
Fixed Block |  | 50 | 48 | Size: 1; Name: Off48; Type: uint16; R/W: RW | M
Fixed Block |  | 51 | 49 | Size: 1; Name: Off49; Type: uint16; R/W: RW | M
Fixed Block |  | 52 | 50 | Size: 1; Name: Off50; Type: uint16; R/W: RW | M
Fixed Block |  | 53 | 51 | 2 | Ts | Timestamp |  | uint32 |  |  | RW | M | Timestamp value is the number of seconds since January 1, 2000
Fixed Block |  | 55 | 53 | 1 | Ms | Milliseconds |  | uint16 |  |  | RW | M | Millisecond counter 0-999
Fixed Block |  | 56 | 54 | 1 | Seq | Sequence |  | uint16 |  |  | RW | M | Sequence number of request | Shall be advanced for each request
Fixed Block |  | 57 | 55 | 1 | Role | Role |  | uint16 |  |  | RW | M | Digital Signature ID | User's role id 0-5
Fixed Block |  | 58 | 56 | 1 | Alg | Algorithm |  | enum16 |  |  | R | M | Algorithm used to compute the digital signature | For future proof
Fixed Block |  | 59 | 57 | 1 | N | N |  | uint16 |  |  | R | M | Number of registers comprising the digital signature. | The value of N must be at least 4 (64 bits)
Repeating Block |  | 60 | 0 | 1 | DS | DS |  | uint16 |  |  | R | M | Digital Signature | The DS covers all registers from X to N and is N registers in length
enum16 | Alg |  |  | Name: NONE; Label: NONE; Value: 0 |  | No digital signature | For test purposes only
enum16 | Alg |  |  | Name: AES-GMAC-64; Label: AES-GMAC-64; Value: 1 |  | 64 bit AES signature algorithm is used
enum16 | Alg |  |  | Name: ECC-256; Label: ECC-256; Value: 2 |  | 256 bit ECC signature algorithm is used

## 4
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Secure Dataset Read Response | 4 | uint16 |  |  | R | M | Compute a digial signature over a specifed set of data registers
Header |  | 1 |  | 1 | L |  | 60 + (RB Count * 1) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | RqSeq | Request Sequence |  | uint16 |  |  | R | M | Sequence number from the request
Fixed Block |  | 3 | 1 | 1 | Sts | Status |  | uint16 |  |  | R | M | Status of last read operation
Fixed Block |  | 4 | 2 | 1 | X | X |  | uint16 |  |  | R | M | Number of values from the request | A max of 50 values are allocated
Fixed Block |  | 5 | 3 | 1 | Val1 | Value1 |  | uint16 |  |  | R | M | Copy of value from register Off1. | Unused values shall return 0xFFFF (unimplemented)
Fixed Block |  | 6 | 4 | Size: 1; Name: Val2; Type: uint16; R/W: R | M
Fixed Block |  | 7 | 5 | Size: 1; Name: Val3; Type: uint16; R/W: R | M
Fixed Block |  | 8 | 6 | Size: 1; Name: Val4; Type: uint16; R/W: R | M
Fixed Block |  | 9 | 7 | Size: 1; Name: Val5; Type: uint16; R/W: R | M
Fixed Block |  | 10 | 8 | Size: 1; Name: Val6; Type: uint16; R/W: R | M
Fixed Block |  | 11 | 9 | Size: 1; Name: Val7; Type: uint16; R/W: R | M
Fixed Block |  | 12 | 10 | Size: 1; Name: Val8; Type: uint16; R/W: R | M
Fixed Block |  | 13 | 11 | Size: 1; Name: Val9; Type: uint16; R/W: R | M
Fixed Block |  | 14 | 12 | Size: 1; Name: Val10; Type: uint16; R/W: R | M
Fixed Block |  | 15 | 13 | Size: 1; Name: Val11; Type: uint16; R/W: R | M
Fixed Block |  | 16 | 14 | Size: 1; Name: Val12; Type: uint16; R/W: R | M
Fixed Block |  | 17 | 15 | Size: 1; Name: Val13; Type: uint16; R/W: R | M
Fixed Block |  | 18 | 16 | Size: 1; Name: Val14; Type: uint16; R/W: R | M
Fixed Block |  | 19 | 17 | Size: 1; Name: Val15; Type: uint16; R/W: R | M
Fixed Block |  | 20 | 18 | Size: 1; Name: Val16; Type: uint16; R/W: R | M
Fixed Block |  | 21 | 19 | Size: 1; Name: Val17; Type: uint16; R/W: R | M
Fixed Block |  | 22 | 20 | Size: 1; Name: Val18; Type: uint16; R/W: R | M
Fixed Block |  | 23 | 21 | Size: 1; Name: Val19; Type: uint16; R/W: R | M
Fixed Block |  | 24 | 22 | Size: 1; Name: Val20; Type: uint16; R/W: R | M
Fixed Block |  | 25 | 23 | Size: 1; Name: Val21; Type: uint16; R/W: R | M
Fixed Block |  | 26 | 24 | Size: 1; Name: Val22; Type: uint16; R/W: R | M
Fixed Block |  | 27 | 25 | Size: 1; Name: Val23; Type: uint16; R/W: R | M
Fixed Block |  | 28 | 26 | Size: 1; Name: Val24; Type: uint16; R/W: R | M
Fixed Block |  | 29 | 27 | Size: 1; Name: Val25; Type: uint16; R/W: R | M
Fixed Block |  | 30 | 28 | Size: 1; Name: Val26; Type: uint16; R/W: R | M
Fixed Block |  | 31 | 29 | Size: 1; Name: Val27; Type: uint16; R/W: R | M
Fixed Block |  | 32 | 30 | Size: 1; Name: Val28; Type: uint16; R/W: R | M
Fixed Block |  | 33 | 31 | Size: 1; Name: Val29; Type: uint16; R/W: R | M
Fixed Block |  | 34 | 32 | Size: 1; Name: Val30; Type: uint16; R/W: R | M
Fixed Block |  | 35 | 33 | Size: 1; Name: Val31; Type: uint16; R/W: R | M
Fixed Block |  | 36 | 34 | Size: 1; Name: Val32; Type: uint16; R/W: R | M
Fixed Block |  | 37 | 35 | Size: 1; Name: Val33; Type: uint16; R/W: R | M
Fixed Block |  | 38 | 36 | Size: 1; Name: Val34; Type: uint16; R/W: R | M
Fixed Block |  | 39 | 37 | Size: 1; Name: Val35; Type: uint16; R/W: R | M
Fixed Block |  | 40 | 38 | Size: 1; Name: Val36; Type: uint16; R/W: R | M
Fixed Block |  | 41 | 39 | Size: 1; Name: Val37; Type: uint16; R/W: R | M
Fixed Block |  | 42 | 40 | Size: 1; Name: Val38; Type: uint16; R/W: R | M
Fixed Block |  | 43 | 41 | Size: 1; Name: Val39; Type: uint16; R/W: R | M
Fixed Block |  | 44 | 42 | Size: 1; Name: Val40; Type: uint16; R/W: R | M
Fixed Block |  | 45 | 43 | Size: 1; Name: Val41; Type: uint16; R/W: R | M
Fixed Block |  | 46 | 44 | Size: 1; Name: Val42; Type: uint16; R/W: R | M
Fixed Block |  | 47 | 45 | Size: 1; Name: Val43; Type: uint16; R/W: R | M
Fixed Block |  | 48 | 46 | Size: 1; Name: Val44; Type: uint16; R/W: R | M
Fixed Block |  | 49 | 47 | Size: 1; Name: Val45; Type: uint16; R/W: R | M
Fixed Block |  | 50 | 48 | Size: 1; Name: Val46; Type: uint16; R/W: R | M
Fixed Block |  | 51 | 49 | Size: 1; Name: Val47; Type: uint16; R/W: R | M
Fixed Block |  | 52 | 50 | Size: 1; Name: Val48; Type: uint16; R/W: R | M
Fixed Block |  | 53 | 51 | Size: 1; Name: Val49; Type: uint16; R/W: R | M
Fixed Block |  | 54 | 52 | Size: 1; Name: Val50; Type: uint16; R/W: R | M
Fixed Block |  | 55 | 53 | 2 | Ts | Timestamp |  | uint32 |  |  | R | M | Timestamp value is the number of seconds since January 1, 2000
Fixed Block |  | 57 | 55 | 1 | Ms | Milliseconds |  | uint16 |  |  | R | M | Millisecond counter 0-999
Fixed Block |  | 58 | 56 | 1 | Seq | Sequence |  | uint16 |  |  | R | M | Sequence number of response | Shall be advanced for each reponse
Fixed Block |  | 59 | 57 | 1 | Alm | Alarm |  | enum16 |  |  | R | M | Bitmask alarm code
Fixed Block |  | 60 | 58 | 1 | Alg | Algorithm |  | enum16 |  |  | R | M | Algorithm used to compute the digital signature | For future proof
Fixed Block |  | 61 | 59 | 1 | N | N |  | uint16 |  |  | R | M | Number of registers comprising the digital signature. | The value of N must be at least 4 (64 bits)
Repeating Block |  | 62 | 0 | 1 | DS | DS |  | uint16 |  |  | R | M | Digital Signature | The DS covers all registers from X to N and is N registers in length
uint16 | Sts |  |  | Name: SUCCESS; Label: SUCCESS; Value: 0 |  | Operation succeeded
uint16 | Sts | [11 empty] | Operation failed digital signature check | bar: Name to Value
uint16 | Sts |  |  | Name: ACL; Label: ACL; Value: 2 |  | Operation failed access control check | One or more registers were not writable by this role
uint16 | Sts |  |  | Name: OFF; Label: OFF; Value: 3 |  | Operation failed offset check | Offset out of range or missing from multi-register value
enum16 | Alm |  |  | Name: NONE; Label: NONE; Value: 0 |  | No digital signature | For test purposes only
enum16 | Alm |  |  | Name: ALM; Label: ALARM; Value: 1 |  | Security Alarm
enum16 | Alg |  |  | Name: NONE; Label: NONE; Value: 0 |  | No digital signature | For test purposes only
enum16 | Alg |  |  | Name: AES-GMAC-64; Label: AES-GMAC-64; Value: 1 |  | 64 bit AES signature algorithm is used
enum16 | Alg |  |  | Name: ECC-256; Label: ECC-256; Value: 2 |  | 256 bit ECC signature algorithm is used

## 5
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Secure Write Request | 5 | uint16 |  |  | R | M | Include a digial signature along with the control data
Header |  | 1 |  | 1 | L |  | 88 + (RB Count * 1) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | X | X |  | uint16 |  |  | RW | M | Number of (offset, value) pairs being written | A max of 50 (offset, value) pairs are allocated
Fixed Block |  | 3 | 1 | 1 | Off1 | Offset1 |  | uint16 |  |  | RW | M | Offset of control register to write value to
Fixed Block |  | 4 | 2 | 1 | Val1 | Value1 |  | uint16 |  |  | RW | M | Value to write to control register at offset
Fixed Block |  | 5 | 3 | Size: 1; Name: Off2; Type: uint16; R/W: RW | M
Fixed Block |  | 6 | 4 | Size: 1; Name: Val2; Type: uint16; R/W: RW | M
Fixed Block |  | 7 | 5 | Size: 1; Name: Off3; Type: uint16; R/W: RW | M
Fixed Block |  | 8 | 6 | Size: 1; Name: Val3; Type: uint16; R/W: RW | M
Fixed Block |  | 9 | 7 | Size: 1; Name: Off4; Type: uint16; R/W: RW | M
Fixed Block |  | 10 | 8 | Size: 1; Name: Val4; Type: uint16; R/W: RW | M
Fixed Block |  | 11 | 9 | Size: 1; Name: Off5; Type: uint16; R/W: RW | M
Fixed Block |  | 12 | 10 | Size: 1; Name: Val5; Type: uint16; R/W: RW | M
Fixed Block |  | 13 | 11 | Size: 1; Name: Off6; Type: uint16; R/W: RW | M
Fixed Block |  | 14 | 12 | Size: 1; Name: Val6; Type: uint16; R/W: RW | M
Fixed Block |  | 15 | 13 | Size: 1; Name: Off7; Type: uint16; R/W: RW | M
Fixed Block |  | 16 | 14 | Size: 1; Name: Val7; Type: uint16; R/W: RW | M
Fixed Block |  | 17 | 15 | Size: 1; Name: Off8; Type: uint16; R/W: RW | M
Fixed Block |  | 18 | 16 | Size: 1; Name: Val8; Type: uint16; R/W: RW | M
Fixed Block |  | 19 | 17 | Size: 1; Name: Off9; Type: uint16; R/W: RW | M
Fixed Block |  | 20 | 18 | Size: 1; Name: Val9; Type: uint16; R/W: RW | M
Fixed Block |  | 21 | 19 | Size: 1; Name: Off10; Type: uint16; R/W: RW | M
Fixed Block |  | 22 | 20 | Size: 1; Name: Val10; Type: uint16; R/W: RW | M
Fixed Block |  | 23 | 21 | Size: 1; Name: Off11; Type: uint16; R/W: RW | M
Fixed Block |  | 24 | 22 | Size: 1; Name: Val11; Type: uint16; R/W: RW | M
Fixed Block |  | 25 | 23 | Size: 1; Name: Off12; Type: uint16; R/W: RW | M
Fixed Block |  | 26 | 24 | Size: 1; Name: Val12; Type: uint16; R/W: RW | M
Fixed Block |  | 27 | 25 | Size: 1; Name: Off13; Type: uint16; R/W: RW | M
Fixed Block |  | 28 | 26 | Size: 1; Name: Val13; Type: uint16; R/W: RW | M
Fixed Block |  | 29 | 27 | Size: 1; Name: Off14; Type: uint16; R/W: RW | M
Fixed Block |  | 30 | 28 | Size: 1; Name: Val14; Type: uint16; R/W: RW | M
Fixed Block |  | 31 | 29 | Size: 1; Name: Off15; Type: uint16; R/W: RW | M
Fixed Block |  | 32 | 30 | Size: 1; Name: Val15; Type: uint16; R/W: RW | M
Fixed Block |  | 33 | 31 | Size: 1; Name: Off16; Type: uint16; R/W: RW | M
Fixed Block |  | 34 | 32 | Size: 1; Name: Val16; Type: uint16; R/W: RW | M
Fixed Block |  | 35 | 33 | Size: 1; Name: Off17; Type: uint16; R/W: RW | M
Fixed Block |  | 36 | 34 | Size: 1; Name: Val17; Type: uint16; R/W: RW | M
Fixed Block |  | 37 | 35 | Size: 1; Name: Off18; Type: uint16; R/W: RW | M
Fixed Block |  | 38 | 36 | Size: 1; Name: Val18; Type: uint16; R/W: RW | M
Fixed Block |  | 39 | 37 | Size: 1; Name: Off19; Type: uint16; R/W: RW | M
Fixed Block |  | 40 | 38 | Size: 1; Name: Val19; Type: uint16; R/W: RW | M
Fixed Block |  | 41 | 39 | Size: 1; Name: Off20; Type: uint16; R/W: RW | M
Fixed Block |  | 42 | 40 | Size: 1; Name: Val20; Type: uint16; R/W: RW | M
Fixed Block |  | 43 | 41 | Size: 1; Name: Off21; Type: uint16; R/W: RW | M
Fixed Block |  | 44 | 42 | Size: 1; Name: Val21; Type: uint16; R/W: RW | M
Fixed Block |  | 45 | 43 | Size: 1; Name: Off22; Type: uint16; R/W: RW | M
Fixed Block |  | 46 | 44 | Size: 1; Name: Val22; Type: uint16; R/W: RW | M
Fixed Block |  | 47 | 45 | Size: 1; Name: Off23; Type: uint16; R/W: RW | M
Fixed Block |  | 48 | 46 | Size: 1; Name: Val23; Type: uint16; R/W: RW | M
Fixed Block |  | 49 | 47 | Size: 1; Name: Off24; Type: uint16; R/W: RW | M
Fixed Block |  | 50 | 48 | Size: 1; Name: Val24; Type: uint16; R/W: RW | M
Fixed Block |  | 51 | 49 | Size: 1; Name: Off25; Type: uint16; R/W: RW | M
Fixed Block |  | 52 | 50 | Size: 1; Name: Val25; Type: uint16; R/W: RW | M
Fixed Block |  | 53 | 51 | Size: 1; Name: Off26; Type: uint16; R/W: RW | M
Fixed Block |  | 54 | 52 | Size: 1; Name: Val26; Type: uint16; R/W: RW | M
Fixed Block |  | 55 | 53 | Size: 1; Name: Off27; Type: uint16; R/W: RW | M
Fixed Block |  | 56 | 54 | Size: 1; Name: Val27; Type: uint16; R/W: RW | M
Fixed Block |  | 57 | 55 | Size: 1; Name: Off28; Type: uint16; R/W: RW | M
Fixed Block |  | 58 | 56 | Size: 1; Name: Val28; Type: uint16; R/W: RW | M
Fixed Block |  | 59 | 57 | Size: 1; Name: Off29; Type: uint16; R/W: RW | M
Fixed Block |  | 60 | 58 | Size: 1; Name: Val29; Type: uint16; R/W: RW | M
Fixed Block |  | 61 | 59 | Size: 1; Name: Off30; Type: uint16; R/W: RW | M
Fixed Block |  | 62 | 60 | Size: 1; Name: Val30; Type: uint16; R/W: RW | M
Fixed Block |  | 63 | 61 | Size: 1; Name: Off31; Type: uint16; R/W: RW | M
Fixed Block |  | 64 | 62 | Size: 1; Name: Val31; Type: uint16; R/W: RW | M
Fixed Block |  | 65 | 63 | Size: 1; Name: Off32; Type: uint16; R/W: RW | M
Fixed Block |  | 66 | 64 | Size: 1; Name: Val32; Type: uint16; R/W: RW | M
Fixed Block |  | 67 | 65 | Size: 1; Name: Off33; Type: uint16; R/W: RW | M
Fixed Block |  | 68 | 66 | Size: 1; Name: Val33; Type: uint16; R/W: RW | M
Fixed Block |  | 69 | 67 | Size: 1; Name: Off34; Type: uint16; R/W: RW | M
Fixed Block |  | 70 | 68 | Size: 1; Name: Val34; Type: uint16; R/W: RW | M
Fixed Block |  | 71 | 69 | Size: 1; Name: Off35; Type: uint16; R/W: RW | M
Fixed Block |  | 72 | 70 | Size: 1; Name: Val35; Type: uint16; R/W: RW | M
Fixed Block |  | 73 | 71 | Size: 1; Name: Off36; Type: uint16; R/W: RW | M
Fixed Block |  | 74 | 72 | Size: 1; Name: Val36; Type: uint16; R/W: RW | M
Fixed Block |  | 75 | 73 | Size: 1; Name: Off37; Type: uint16; R/W: RW | M
Fixed Block |  | 76 | 74 | Size: 1; Name: Val37; Type: uint16; R/W: RW | M
Fixed Block |  | 77 | 75 | Size: 1; Name: Off38; Type: uint16; R/W: RW | M
Fixed Block |  | 78 | 76 | Size: 1; Name: Val38; Type: uint16; R/W: RW | M
Fixed Block |  | 79 | 77 | Size: 1; Name: Off39; Type: uint16; R/W: RW | M
Fixed Block |  | 80 | 78 | Size: 1; Name: Val39; Type: uint16; R/W: RW | M
Fixed Block |  | 81 | 79 | Size: 1; Name: Off40; Type: uint16; R/W: RW | M
Fixed Block |  | 82 | 80 | Size: 1; Name: Val40; Type: uint16; R/W: RW | M
Fixed Block |  | 83 | 81 | 2 | Ts | Timestamp |  | uint32 |  |  | RW | M | Timestamp value is the number of seconds since January 1, 2000
Fixed Block |  | 85 | 83 | 1 | Ms | Milliseconds |  | uint16 |  |  | RW | M | Millisecond counter 0-999
Fixed Block |  | 86 | 84 | 1 | Seq | Sequence |  | uint16 |  |  | RW | M | Sequence number of request | Shall be advanced for each request
Fixed Block |  | 87 | 85 | 1 | Role | Role |  | uint16 |  |  | RW | M | Signing key used 0-5 | Each controller is assigned a key index that maps to their access control role
Fixed Block |  | 88 | 86 | 1 | Alg | Algorithm |  | enum16 |  |  | RW | M | Algorithm used to compute the digital signature | For future proof
Fixed Block |  | 89 | 87 | 1 | N | N |  | uint16 |  |  | RW | M | Number of registers comprising the digital signature. | The value of N must be at least 4 (64 bits)
Repeating Block |  | 90 | 0 | 1 | DS | DS |  | uint16 |  |  | RW | O | Digital Signature | The DS covers all registers from X to N and is N registers in length
enum16 | Alg |  |  | Name: NONE; Label: NONE; Value: 0 |  | No digital signature | For test purposes only
enum16 | Alg |  |  | Name: AES-GMAC-64; Label: AES-GMAC-64; Value: 1 |  | 64 bit AES signature algorithm is used
enum16 | Alg |  |  | Name: ECC-256; Label: ECC-256; Value: 2 |  | 256 bit ECC signature algorithm is used

## 6
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Secure Write Sequential Request | 6 | uint16 |  |  | R | M | Include a digial signature along with the control data
Header |  | 1 |  | 1 | L |  | 90 + (RB Count * 1) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | X | X |  | uint16 |  |  | RW | M | Number of (offset, value) pairs being written | A max of 50 (offset, value) pairs are allocated
Fixed Block |  | 3 | 1 | 1 | Off | Offset |  | uint16 |  |  | RW | M | Starting offset for write operation | X values to follow
Fixed Block |  | 4 | 2 | 1 | Val1 | Value1 |  | uint16 |  |  | RW | M | Value to write to control register at offset
Fixed Block |  | 5 | 3 | Size: 1; Name: Val2; Type: uint16; R/W: RW | M
Fixed Block |  | 6 | 4 | Size: 1; Name: Val3; Type: uint16; R/W: RW | M
Fixed Block |  | 7 | 5 | Size: 1; Name: Val4; Type: uint16; R/W: RW | M
Fixed Block |  | 8 | 6 | Size: 1; Name: Val5; Type: uint16; R/W: RW | M
Fixed Block |  | 9 | 7 | Size: 1; Name: Val6; Type: uint16; R/W: RW | M
Fixed Block |  | 10 | 8 | Size: 1; Name: Val7; Type: uint16; R/W: RW | M
Fixed Block |  | 11 | 9 | Size: 1; Name: Val8; Type: uint16; R/W: RW | M
Fixed Block |  | 12 | 10 | Size: 1; Name: Val9; Type: uint16; R/W: RW | M
Fixed Block |  | 13 | 11 | Size: 1; Name: Val10; Type: uint16; R/W: RW | M
Fixed Block |  | 14 | 12 | Size: 1; Name: Val11; Type: uint16; R/W: RW | M
Fixed Block |  | 15 | 13 | Size: 1; Name: Val12; Type: uint16; R/W: RW | M
Fixed Block |  | 16 | 14 | Size: 1; Name: Val13; Type: uint16; R/W: RW | M
Fixed Block |  | 17 | 15 | Size: 1; Name: Val14; Type: uint16; R/W: RW | M
Fixed Block |  | 18 | 16 | Size: 1; Name: Val15; Type: uint16; R/W: RW | M
Fixed Block |  | 19 | 17 | Size: 1; Name: Val16; Type: uint16; R/W: RW | M
Fixed Block |  | 20 | 18 | Size: 1; Name: Val17; Type: uint16; R/W: RW | M
Fixed Block |  | 21 | 19 | Size: 1; Name: Val18; Type: uint16; R/W: RW | M
Fixed Block |  | 22 | 20 | Size: 1; Name: Val19; Type: uint16; R/W: RW | M
Fixed Block |  | 23 | 21 | Size: 1; Name: Val20; Type: uint16; R/W: RW | M
Fixed Block |  | 24 | 22 | Size: 1; Name: Val21; Type: uint16; R/W: RW | M
Fixed Block |  | 25 | 23 | Size: 1; Name: Val22; Type: uint16; R/W: RW | M
Fixed Block |  | 26 | 24 | Size: 1; Name: Val23; Type: uint16; R/W: RW | M
Fixed Block |  | 27 | 25 | Size: 1; Name: Val24; Type: uint16; R/W: RW | M
Fixed Block |  | 28 | 26 | Size: 1; Name: Val25; Type: uint16; R/W: RW | M
Fixed Block |  | 29 | 27 | Size: 1; Name: Val26; Type: uint16; R/W: RW | M
Fixed Block |  | 30 | 28 | Size: 1; Name: Val27; Type: uint16; R/W: RW | M
Fixed Block |  | 31 | 29 | Size: 1; Name: Val28; Type: uint16; R/W: RW | M
Fixed Block |  | 32 | 30 | Size: 1; Name: Val29; Type: uint16; R/W: RW | M
Fixed Block |  | 33 | 31 | Size: 1; Name: Val30; Type: uint16; R/W: RW | M
Fixed Block |  | 34 | 32 | Size: 1; Name: Val31; Type: uint16; R/W: RW | M
Fixed Block |  | 35 | 33 | Size: 1; Name: Val32; Type: uint16; R/W: RW | M
Fixed Block |  | 36 | 34 | Size: 1; Name: Val33; Type: uint16; R/W: RW | M
Fixed Block |  | 37 | 35 | Size: 1; Name: Val34; Type: uint16; R/W: RW | M
Fixed Block |  | 38 | 36 | Size: 1; Name: Val35; Type: uint16; R/W: RW | M
Fixed Block |  | 39 | 37 | Size: 1; Name: Val36; Type: uint16; R/W: RW | M
Fixed Block |  | 40 | 38 | Size: 1; Name: Val37; Type: uint16; R/W: RW | M
Fixed Block |  | 41 | 39 | Size: 1; Name: Val38; Type: uint16; R/W: RW | M
Fixed Block |  | 42 | 40 | Size: 1; Name: Val39; Type: uint16; R/W: RW | M
Fixed Block |  | 43 | 41 | Size: 1; Name: Val40; Type: uint16; R/W: RW | M
Fixed Block |  | 44 | 42 | Size: 1; Name: Val41; Type: uint16; R/W: RW | M
Fixed Block |  | 45 | 43 | Size: 1; Name: Val42; Type: uint16; R/W: RW | M
Fixed Block |  | 46 | 44 | Size: 1; Name: Val43; Type: uint16; R/W: RW | M
Fixed Block |  | 47 | 45 | Size: 1; Name: Val44; Type: uint16; R/W: RW | M
Fixed Block |  | 48 | 46 | Size: 1; Name: Val45; Type: uint16; R/W: RW | M
Fixed Block |  | 49 | 47 | Size: 1; Name: Val46; Type: uint16; R/W: RW | M
Fixed Block |  | 50 | 48 | Size: 1; Name: Val47; Type: uint16; R/W: RW | M
Fixed Block |  | 51 | 49 | Size: 1; Name: Val48; Type: uint16; R/W: RW | M
Fixed Block |  | 52 | 50 | Size: 1; Name: Val49; Type: uint16; R/W: RW | M
Fixed Block |  | 53 | 51 | Size: 1; Name: Val50; Type: uint16; R/W: RW | M
Fixed Block |  | 54 | 52 | Size: 1; Name: Val51; Type: uint16; R/W: RW | M
Fixed Block |  | 55 | 53 | Size: 1; Name: Val52; Type: uint16; R/W: RW | M
Fixed Block |  | 56 | 54 | Size: 1; Name: Val53; Type: uint16; R/W: RW | M
Fixed Block |  | 57 | 55 | Size: 1; Name: Val54; Type: uint16; R/W: RW | M
Fixed Block |  | 58 | 56 | Size: 1; Name: Val55; Type: uint16; R/W: RW | M
Fixed Block |  | 59 | 57 | Size: 1; Name: Val56; Type: uint16; R/W: RW | M
Fixed Block |  | 60 | 58 | Size: 1; Name: Val57; Type: uint16; R/W: RW | M
Fixed Block |  | 61 | 59 | Size: 1; Name: Val58; Type: uint16; R/W: RW | M
Fixed Block |  | 62 | 60 | Size: 1; Name: Val59; Type: uint16; R/W: RW | M
Fixed Block |  | 63 | 61 | Size: 1; Name: Val60; Type: uint16; R/W: RW | M
Fixed Block |  | 64 | 62 | Size: 1; Name: Val61; Type: uint16; R/W: RW | M
Fixed Block |  | 65 | 63 | Size: 1; Name: Val62; Type: uint16; R/W: RW | M
Fixed Block |  | 66 | 64 | Size: 1; Name: Val63; Type: uint16; R/W: RW | M
Fixed Block |  | 67 | 65 | Size: 1; Name: Val64; Type: uint16; R/W: RW | M
Fixed Block |  | 68 | 66 | Size: 1; Name: Val65; Type: uint16; R/W: RW | M
Fixed Block |  | 69 | 67 | Size: 1; Name: Val66; Type: uint16; R/W: RW | M
Fixed Block |  | 70 | 68 | Size: 1; Name: Val67; Type: uint16; R/W: RW | M
Fixed Block |  | 71 | 69 | Size: 1; Name: Val68; Type: uint16; R/W: RW | M
Fixed Block |  | 72 | 70 | Size: 1; Name: Val69; Type: uint16; R/W: RW | M
Fixed Block |  | 73 | 71 | Size: 1; Name: Val70; Type: uint16; R/W: RW | M
Fixed Block |  | 74 | 72 | Size: 1; Name: Val71; Type: uint16; R/W: RW | M
Fixed Block |  | 75 | 73 | Size: 1; Name: Val72; Type: uint16; R/W: RW | M
Fixed Block |  | 76 | 74 | Size: 1; Name: Val73; Type: uint16; R/W: RW | M
Fixed Block |  | 77 | 75 | Size: 1; Name: Val74; Type: uint16; R/W: RW | M
Fixed Block |  | 78 | 76 | Size: 1; Name: Val75; Type: uint16; R/W: RW | M
Fixed Block |  | 79 | 77 | Size: 1; Name: Val76; Type: uint16; R/W: RW | M
Fixed Block |  | 80 | 78 | Size: 1; Name: Val77; Type: uint16; R/W: RW | M
Fixed Block |  | 81 | 79 | Size: 1; Name: Val78; Type: uint16; R/W: RW | M
Fixed Block |  | 82 | 80 | Size: 1; Name: Val79; Type: uint16; R/W: RW | M
Fixed Block |  | 83 | 81 | Size: 1; Name: Val80; Type: uint16; R/W: RW | M
Fixed Block |  | 84 | 82 | 2 | Ts | Timestamp |  | uint32 |  |  | RW | M | Timestamp value is the number of seconds since January 1, 2000
Fixed Block |  | 86 | 84 | 1 | Ms | Milliseconds |  | uint16 |  |  | RW | M | Millisecond counter 0-999
Fixed Block |  | 87 | 85 | 1 | Seq | Sequence |  | uint16 |  |  | RW | M | Sequence number of request | Shall be advanced for each request
Fixed Block |  | 88 | 86 | 1 | Role | Role |  | uint16 |  |  | RW | M | Signing key used 0-5 | Each controller is assigned a key index that maps to their access control role
Fixed Block |  | 89 | 87 | Size: 1; Name: Rsrvd; Type: pad; R/W: RW | M
Fixed Block |  | 90 | 88 | 1 | Alg | Algorithm |  | enum16 |  |  | RW | M | Algorithm used to compute the digital signature | For future proof
Fixed Block |  | 91 | 89 | 1 | N | N |  | uint16 |  |  | RW | M | Number of registers comprising the digital signature. | The value of N must be at least 4 (64 bits)
Repeating Block |  | 92 | 0 | 1 | DS | DS |  | uint16 |  |  | RW | O | Digital Signature | The DS covers all registers from X to N and is N registers in length
enum16 | Alg |  |  | Name: NONE; Label: NONE; Value: 0 |  | No digital signature | For test purposes only
enum16 | Alg |  |  | Name: AES-GMAC-64; Label: AES-GMAC-64; Value: 1 |  | 64 bit AES signature algorithm is used
enum16 | Alg |  |  | Name: ECC-256; Label: ECC-256; Value: 2 |  | 256 bit ECC signature algorithm is used

## 7
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Secure Write Response Model (DRAFT 1) | 7 | uint16 |  |  | R | M | Include a digital signature over the response | Used in conjunction with a Secure Write Request
Header |  | 1 |  | 1 | L |  | 10 + (RB Count * 1) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | RqSeq | Request Sequence |  | uint16 |  |  | R | M | Sequence number from the request
Fixed Block |  | 3 | 1 | 1 | Sts | Status |  | enum16 |  |  | R | M | Status of last write operation
Fixed Block |  | 4 | 2 | 2 | Ts | Timestamp |  | uint32 |  |  | R | M | Timestamp value is the number of seconds since January 1, 2000
Fixed Block |  | 6 | 4 | 1 | Ms | Milliseconds |  | uint16 |  |  | R | M | Millisecond counter 0-999
Fixed Block |  | 7 | 5 | 1 | Seq | Sequence |  | uint16 |  |  | R | M | Sequence number of response | Shall be advanced for each reponse
Fixed Block |  | 8 | 6 | 1 | Alm | Alarm |  | enum16 |  |  | R | M | Bitmask alarm code
Fixed Block |  | 9 | 7 | Size: 1; Name: Rsrvd; Type: pad; R/W: R | M
Fixed Block |  | 10 | 8 | 1 | Alg | Algorithm |  | enum16 |  |  | R | M | Algorithm used to compute the digital signature | For future proof
Fixed Block |  | 11 | 9 | 1 | N | N |  | uint16 |  |  | RW | M | Number of registers comprising the digital signature. | The value of N must be at least 4 (64 bits)
Repeating Block |  | 12 | 0 | 1 | DS | DS |  | uint16 |  |  | RW | O | Digital Signature | The DS covers all registers from X to N and is N registers in length
enum16 | Sts |  |  | Name: SUCCESS; Label: SUCCESS; Value: 0 |  | Operation succeeded
enum16 | Sts | [11 empty] | Operation failed digital signature check | The signature was not valid | bar: Name to Value
enum16 | Sts |  |  | Name: ACL; Label: ACL; Value: 2 |  | Operation failed access control check | One or more registers were not writable by this role
enum16 | Sts |  |  | Name: OFF; Label: OFF; Value: 3 |  | Operation failed offset check | Offset out of range or missing from multi-register value
enum16 | Sts |  |  | Name: VAL; Label: VAL; Value: 4 |  | Operation failed valid value check | Value is out of acceptable range
enum16 | Alm |  |  | Name: NONE; Label: NONE; Value: 0 |  | No Alarms | For test purposes only
enum16 | Alm |  |  | Name: ALM; Label: ALARM; Value: 1 |  | Security Alarm
enum16 | Alg |  |  | Name: NONE; Label: NONE; Value: 0 |  | No Alarms | For test purposes only
enum16 | Alg |  |  | Name: AES-GMAC-64; Label: AES-GMAC-64; Value: 1 |  | 64 bit AES signature algorithm is used
enum16 | Alg |  |  | Name: ECC-256; Label: ECC-256; Value: 2 |  | 256 bit ECC signature algorithm is used

## 8
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Get Device Security Certificate | 8 | uint16 |  |  | R | M | Security model for PKI
Header |  | 1 |  | 1 | L |  | 2 + (RB Count * 1) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | Fmt | Format |  | enum16 |  |  | R | M | X.509 format of the certificate. DER or PEM.
Fixed Block |  | 3 | 1 | 1 | N | N |  | uint16 |  |  | R | M | Number of registers to follow for the certificate
Repeating Block |  | 4 | 0 | 1 | Cert | Cert |  | uint16 |  |  | R | M | X.509 Certificate of the device
enum16 | Fmt |  |  | Name: NONE; Label: NONE; Value: 0
enum16 | Fmt |  |  | Name: X509_PEM; Label: PEM; Value: 1
enum16 | Fmt |  |  | Name: X509_DER; Label: DER; Value: 2

## 9
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Set Operator Security Certificate | 9 | uint16 |  |  | R | M | Security model for PKI
Header |  | 1 |  | 1 | L |  | 92 + (RB Count * 1) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | CertUID | Cert_UID |  | uint16 |  |  | RW | M | User ID for this certificate
Fixed Block |  | 3 | 1 | 1 | CertRole | Cert_Role |  | uint16 |  |  | RW | M | Role for this certificate
Fixed Block |  | 4 | 2 | 1 | Fmt | Format |  | enum16 |  |  | RW | M | Format of this certificate
Fixed Block |  | 5 | 3 | 1 | Typ | Type |  | enum16 |  |  | RW | M | Type of this certificate
Fixed Block |  | 6 | 4 | 1 | TotLn | Total Length |  | uint16 |  |  | RW | M | Total Length of the Certificate | In registers, zero padded.
Fixed Block |  | 7 | 5 | 1 | FrgLn | Fragment length |  | uint16 |  |  | RW | M | Length of this fragment | Maximum fragment length is 80 registers
Fixed Block |  | 8 | 6 | 1 | Frg1 | Frag1 |  | uint16 |  |  | RW | M | First word of this fragment
Fixed Block |  | 9 | 7 | Size: 1; Name: Frg2; Type: uint16; R/W: RW | M
Fixed Block |  | 10 | 8 | Size: 1; Name: Frg3; Type: uint16; R/W: RW | M
Fixed Block |  | 11 | 9 | Size: 1; Name: Frg4; Type: uint16; R/W: RW | M
Fixed Block |  | 12 | 10 | Size: 1; Name: Frg5; Type: uint16; R/W: RW | M
Fixed Block |  | 13 | 11 | Size: 1; Name: Frg6; Type: uint16; R/W: RW | M
Fixed Block |  | 14 | 12 | Size: 1; Name: Frg7; Type: uint16; R/W: RW | M
Fixed Block |  | 15 | 13 | Size: 1; Name: Frg8; Type: uint16; R/W: RW | M
Fixed Block |  | 16 | 14 | Size: 1; Name: Frg9; Type: uint16; R/W: RW | M
Fixed Block |  | 17 | 15 | Size: 1; Name: Frg10; Type: uint16; R/W: RW | M
Fixed Block |  | 18 | 16 | Size: 1; Name: Frg11; Type: uint16; R/W: RW | M
Fixed Block |  | 19 | 17 | Size: 1; Name: Frg12; Type: uint16; R/W: RW | M
Fixed Block |  | 20 | 18 | Size: 1; Name: Frg13; Type: uint16; R/W: RW | M
Fixed Block |  | 21 | 19 | Size: 1; Name: Frg14; Type: uint16; R/W: RW | M
Fixed Block |  | 22 | 20 | Size: 1; Name: Frg15; Type: uint16; R/W: RW | M
Fixed Block |  | 23 | 21 | Size: 1; Name: Frg16; Type: uint16; R/W: RW | M
Fixed Block |  | 24 | 22 | Size: 1; Name: Frg17; Type: uint16; R/W: RW | M
Fixed Block |  | 25 | 23 | Size: 1; Name: Frg18; Type: uint16; R/W: RW | M
Fixed Block |  | 26 | 24 | Size: 1; Name: Frg19; Type: uint16; R/W: RW | M
Fixed Block |  | 27 | 25 | Size: 1; Name: Frg20; Type: uint16; R/W: RW | M
Fixed Block |  | 28 | 26 | Size: 1; Name: Frg21; Type: uint16; R/W: RW | M
Fixed Block |  | 29 | 27 | Size: 1; Name: Frg22; Type: uint16; R/W: RW | M
Fixed Block |  | 30 | 28 | Size: 1; Name: Frg23; Type: uint16; R/W: RW | M
Fixed Block |  | 31 | 29 | Size: 1; Name: Frg24; Type: uint16; R/W: RW | M
Fixed Block |  | 32 | 30 | Size: 1; Name: Frg25; Type: uint16; R/W: RW | M
Fixed Block |  | 33 | 31 | Size: 1; Name: Frg26; Type: uint16; R/W: RW | M
Fixed Block |  | 34 | 32 | Size: 1; Name: Frg27; Type: uint16; R/W: RW | M
Fixed Block |  | 35 | 33 | Size: 1; Name: Frg28; Type: uint16; R/W: RW | M
Fixed Block |  | 36 | 34 | Size: 1; Name: Frg29; Type: uint16; R/W: RW | M
Fixed Block |  | 37 | 35 | Size: 1; Name: Frg30; Type: uint16; R/W: RW | M
Fixed Block |  | 38 | 36 | Size: 1; Name: Frg31; Type: uint16; R/W: RW | M
Fixed Block |  | 39 | 37 | Size: 1; Name: Frg32; Type: uint16; R/W: RW | M
Fixed Block |  | 40 | 38 | Size: 1; Name: Frg33; Type: uint16; R/W: RW | M
Fixed Block |  | 41 | 39 | Size: 1; Name: Frg34; Type: uint16; R/W: RW | M
Fixed Block |  | 42 | 40 | Size: 1; Name: Frg35; Type: uint16; R/W: RW | M
Fixed Block |  | 43 | 41 | Size: 1; Name: Frg36; Type: uint16; R/W: RW | M
Fixed Block |  | 44 | 42 | Size: 1; Name: Frg37; Type: uint16; R/W: RW | M
Fixed Block |  | 45 | 43 | Size: 1; Name: Frg38; Type: uint16; R/W: RW | M
Fixed Block |  | 46 | 44 | Size: 1; Name: Frg39; Type: uint16; R/W: RW | M
Fixed Block |  | 47 | 45 | Size: 1; Name: Frg40; Type: uint16; R/W: RW | M
Fixed Block |  | 48 | 46 | Size: 1; Name: Frg41; Type: uint16; R/W: RW | M
Fixed Block |  | 49 | 47 | Size: 1; Name: Frg42; Type: uint16; R/W: RW | M
Fixed Block |  | 50 | 48 | Size: 1; Name: Frg43; Type: uint16; R/W: RW | M
Fixed Block |  | 51 | 49 | Size: 1; Name: Frg44; Type: uint16; R/W: RW | M
Fixed Block |  | 52 | 50 | Size: 1; Name: Frg45; Type: uint16; R/W: RW | M
Fixed Block |  | 53 | 51 | Size: 1; Name: Frg46; Type: uint16; R/W: RW | M
Fixed Block |  | 54 | 52 | Size: 1; Name: Frg47; Type: uint16; R/W: RW | M
Fixed Block |  | 55 | 53 | Size: 1; Name: Frg48; Type: uint16; R/W: RW | M
Fixed Block |  | 56 | 54 | Size: 1; Name: Frg49; Type: uint16; R/W: RW | M
Fixed Block |  | 57 | 55 | Size: 1; Name: Frg50; Type: uint16; R/W: RW | M
Fixed Block |  | 58 | 56 | Size: 1; Name: Frg51; Type: uint16; R/W: RW | M
Fixed Block |  | 59 | 57 | Size: 1; Name: Frg52; Type: uint16; R/W: RW | M
Fixed Block |  | 60 | 58 | Size: 1; Name: Frg53; Type: uint16; R/W: RW | M
Fixed Block |  | 61 | 59 | Size: 1; Name: Frg54; Type: uint16; R/W: RW | M
Fixed Block |  | 62 | 60 | Size: 1; Name: Frg55; Type: uint16; R/W: RW | M
Fixed Block |  | 63 | 61 | Size: 1; Name: Frg56; Type: uint16; R/W: RW | M
Fixed Block |  | 64 | 62 | Size: 1; Name: Frg57; Type: uint16; R/W: RW | M
Fixed Block |  | 65 | 63 | Size: 1; Name: Frg58; Type: uint16; R/W: RW | M
Fixed Block |  | 66 | 64 | Size: 1; Name: Frg59; Type: uint16; R/W: RW | M
Fixed Block |  | 67 | 65 | Size: 1; Name: Frg60; Type: uint16; R/W: RW | M
Fixed Block |  | 68 | 66 | Size: 1; Name: Frg61; Type: uint16; R/W: RW | M
Fixed Block |  | 69 | 67 | Size: 1; Name: Frg62; Type: uint16; R/W: RW | M
Fixed Block |  | 70 | 68 | Size: 1; Name: Frg63; Type: uint16; R/W: RW | M
Fixed Block |  | 71 | 69 | Size: 1; Name: Frg64; Type: uint16; R/W: RW | M
Fixed Block |  | 72 | 70 | Size: 1; Name: Frg65; Type: uint16; R/W: RW | M
Fixed Block |  | 73 | 71 | Size: 1; Name: Frg66; Type: uint16; R/W: RW | M
Fixed Block |  | 74 | 72 | Size: 1; Name: Frg67; Type: uint16; R/W: RW | M
Fixed Block |  | 75 | 73 | Size: 1; Name: Frg68; Type: uint16; R/W: RW | M
Fixed Block |  | 76 | 74 | Size: 1; Name: Frg69; Type: uint16; R/W: RW | M
Fixed Block |  | 77 | 75 | Size: 1; Name: Frg70; Type: uint16; R/W: RW | M
Fixed Block |  | 78 | 76 | Size: 1; Name: Frg71; Type: uint16; R/W: RW | M
Fixed Block |  | 79 | 77 | Size: 1; Name: Frg72; Type: uint16; R/W: RW | M
Fixed Block |  | 80 | 78 | Size: 1; Name: Frg73; Type: uint16; R/W: RW | M
Fixed Block |  | 81 | 79 | Size: 1; Name: Frg74; Type: uint16; R/W: RW | M
Fixed Block |  | 82 | 80 | Size: 1; Name: Frg75; Type: uint16; R/W: RW | M
Fixed Block |  | 83 | 81 | Size: 1; Name: Frg78; Type: uint16; R/W: RW | M
Fixed Block |  | 84 | 82 | Size: 1; Name: Frg79; Type: uint16; R/W: RW | M
Fixed Block |  | 85 | 83 | 1 | Frg80 | Frag80 |  | uint16 |  |  | RW | M | Last word of this fragment
Fixed Block |  | 86 | 84 | 2 | Ts | Timestamp |  | uint32 |  |  | RW | M | Timestamp value is the number of seconds since January 1, 2000
Fixed Block |  | 88 | 86 | 1 | Ms | Milliseconds |  | uint16 |  |  | RW | M | Millisecond counter 0-999
Fixed Block |  | 89 | 87 | 1 | Seq | Sequence |  | uint16 |  |  | RW | M | Sequence number of request | Shall be advanced for each request
Fixed Block |  | 90 | 88 | 1 | UID | UID |  | uint16 |  |  | RW | M | User ID for the request signature
Fixed Block |  | 91 | 89 | 1 | Role | Role |  | uint16 |  |  | RW | M | Signing key used 0-5 | Each controller is assigned a key index that maps to their access control role
Fixed Block |  | 92 | 90 | 1 | Alg | Algorithm |  | enum16 |  |  | RW | M | Algorithm used to compute the digital signature | For future proof
Fixed Block |  | 93 | 91 | 1 | N | N |  | uint16 |  |  | RW | M | Number of registers to follow for the certificate
Repeating Block |  | 94 | 0 | Size: 1; Name: Cert; Type: uint16; R/W: RW | M
enum16 | Fmt |  |  | Name: NONE; Label: NONE; Value: 0 |  | No digital signature | For test purposes only
enum16 | Fmt |  |  | Name: X509_PEM; Label: PEM; Value: 1
enum16 | Fmt |  |  | Name: X509_DER; Label: DER; Value: 2
enum16 | Typ |  |  | Name: DEV_KEY_PAIR; Value: 0
enum16 | Typ |  |  | Name: DEV_SHARED_KEY; Value: 1
enum16 | Typ |  |  | Name: OPERATOR_PUB; Value: 2
enum16 | Typ |  |  | Name: OPERATOR_SHARED; Value: 3
enum16 | Typ |  |  | Name: CA_PUB; Value: 4
enum16 | Alg |  |  | Name: NONE; Label: NONE; Value: 0 |  | No digital signature | For test purposes only
enum16 | Alg |  |  | Name: AES-GMAC-64; Label: AES-GMAC-64; Value: 1 |  | 64 bit AES signature algorithm is used
enum16 | Alg |  |  | Name: ECC-256; Label: ECC-256; Value: 2 |  | 256 bit ECC signature algorithm is used

## 10
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Communication Interface Header | 10 | uint16 |  |  | R | M | To be included first for a complete interface description
Header |  | 1 |  | 1 | L |  | 4 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | St | Interface Status |  | enum16 |  |  | R | M | Overall interface status
Fixed Block |  | 3 | 1 | 1 | Ctl | Interface Control |  | uint16 |  |  | RW | O | Overall interface control (TBD)
Fixed Block |  | 4 | 2 | 1 | Typ | Physical Access Type |  | enum16 |  |  | R | O | Enumerated value. Type of physical media
Fixed Block |  | 5 | 3 | Size: 1; Name: Pad; Type: pad; R/W: R | O
enum16 | St |  |  | Name: DOWN; Label: down; Value: 0 |  | Interface is down
enum16 | St |  |  | Name: UP; Label: up; Value: 1 |  | Interface is up
enum16 | St |  |  | Name: FAULT; Label: fault; Value: 2 |  | Interface is in a fault state
enum16 | Typ |  |  | Name: UNKNOWN; Label: unknown; Value: 0 |  | Unkown media
enum16 | Typ |  |  | Name: INTERNAL; Label: internal; Value: 1 |  | Internal e.g. embbedded switch
enum16 | Typ |  |  | Name: TWISTED_PAIR; Label: twisted pair; Value: 2 |  | Twisted Pair
enum16 | Typ |  |  | Name: FIBER; Label: fiber; Value: 3 |  | Fiber
enum16 | Typ |  |  | Name: WIRELESS; Value: 4
enum16 | Typ |  |  | Label: wifi; Value: 4 |  | WIFI

## 11
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Ethernet Link Layer | 11 | uint16 |  |  | R | M | Include to support a wired ethernet port
Header |  | 1 |  | 1 | L |  | 13 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | Spd | Ethernet Link Speed |  | uint16 | Mbps |  | R | M | Interface speed in Mb/s
Fixed Block |  | 3 | 1 | 1 | CfgSt | Interface Status Flags |  | bitfield16 |  |  | R | M | Bitmask values Interface flags.
Fixed Block |  | 4 | 2 | 1 | St | Link State |  | enum16 |  |  | R | M | Enumerated value. State information for this interface
Fixed Block |  | 5 | 3 | 4 | MAC | MAC |  | eui48 |  |  | R | O | IEEE MAC address of this interface
Fixed Block |  | 9 | 7 | 4 | Nam | Name |  | string |  |  | RW | O | Interface name (8 chars)
Fixed Block |  | 13 | 11 | 1 | Ctl | Control |  | bitfield16 |  |  | RW | O | Control flags
Fixed Block |  | 14 | 12 | 1 | FrcSpd | Forced Speed |  | uint16 | Mbps |  | RW | O | Forced interface speed in Mb/s when AUTO is disabled
bitfield16 | CfgSt |  |  | Name: LINK; Label: link status; Value: 0 |  | link is up
bitfield16 | CfgSt |  |  | Name: FULL_DUPLEX; Label: duplex; Value: 1 |  | Force full duplex
bitfield16 | CfgSt |  |  | Name: AUTO_NEG1; Label: auto negotiation 1; Value: 2 |  | Auto-negotiation bits are encoded as: 000 - inprogress. 001 - speed detection has failed. 010 - negotiation has failed. 011 - negotiated speed and duplex. 100 - negotiation not attempted.
bitfield16 | CfgSt |  |  | Name: AUTO_NEG2; Label: auto negotiation 2; Value: 3 |  | See AUTO_NEG1
bitfield16 | CfgSt |  |  | Name: AUTO_NEG3; Label: auto negotiation 3; Value: 4 |  | See AUTO_NEG1
bitfield16 | CfgSt |  |  | Name: RESET_REQUIRED; Label: reset required; Value: 5 |  | Setting requires reset
bitfield16 | CfgSt |  |  | Name: HW_FAULT; Label: hw fault; Value: 6 |  | Hardware fault
enum16 | St |  |  | Name: UNKNOWN; Label: unknown; Value: 0 |  | Unknown state
enum16 | St |  |  | Name: ENABLED; Label: enabled; Value: 1 |  | Link is enabled and read
enum16 | St |  |  | Name: DISABLED; Label: disabled; Value: 2 |  | Link is disabled
enum16 | St |  |  | Name: TESTING; Label: testing; Value: 3 |  | Link is in test
bitfield16 | Ctl |  |  | Name: AUTO; Label: auto; Value: 0 |  | Enable auto-negotiatition
bitfield16 | Ctl |  |  | Name: FULL_DUPLEX; Label: duplex; Value: 1 |  | Force full duplex

## 12
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | IPv4 | 12 | uint16 |  |  | R | M | Include to support an IPv4 protocol stack on this interface
Header |  | 1 |  | 1 | L |  | 98 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 4 | Nam | Name |  | string |  |  | RW | O | Interface name
Fixed Block |  | 6 | 4 | 1 | CfgSt | Config Status |  | enum16 |  |  | R | M | Enumerated value. Configuration status
Fixed Block |  | 7 | 5 | 1 | ChgSt | Change Status |  | bitfield16 |  |  | R | M | Bitmask value. A configuration change is pending
Fixed Block |  | 8 | 6 | 1 | Cap | Config Capability |  | bitfield16 |  |  | R | M | Bitmask value. Identify capable sources of configuration
Fixed Block |  | 9 | 7 | 1 | Cfg | IPv4 Config |  | enum16 |  |  | RW | M | Enumerated value. Configuration method used.
Fixed Block |  | 10 | 8 | 1 | Ctl | Control |  | enum16 |  |  | RW | M | Configure use of services
Fixed Block |  | 11 | 9 | 8 | Addr | IP |  | string |  |  | RW | M | IPv4 numeric address as a dotted string xxx.xxx.xxx.xxx
Fixed Block |  | 19 | 17 | 8 | Msk | Netmask |  | string |  |  | RW | M | IPv4 numeric netmask as a dotted string xxx.xxx.xxx.xxx
Fixed Block |  | 27 | 25 | 8 | Gw | Gateway |  | string |  |  | RW | O | IPv4 numeric gateway address as a dotted string xxx.xxx.xxx.xxx
Fixed Block |  | 35 | 33 | 8 | DNS1 | DNS1 |  | string |  |  | RW | O | IPv4 numeric DNS address as a dotted string xxx.xxx.xxx.xxx
Fixed Block |  | 43 | 41 | 8 | DNS2 | DNS2 |  | string |  |  | RW | O | IPv4 numeric DNS address as a dotted string xxx.xxx.xxx.xxx
Fixed Block |  | 51 | 49 | 12 | NTP1 | NTP1 |  | string |  |  | RW | O | IPv4 numeric NTP address as a dotted string xxx.xxx.xxx.xxx
Fixed Block |  | 63 | 61 | 12 | NTP2 | NTP2 |  | string |  |  | RW | O | IPv4 numeric NTP address as a dotted string xxx.xxx.xxx.xxx
Fixed Block |  | 75 | 73 | 12 | DomNam | Domain |  | string |  |  | RW | O | Domain name (24 chars max)
Fixed Block |  | 87 | 85 | 12 | HostNam | Host Name |  | string |  |  | RW | O | Host name (24 chars max)
Fixed Block |  | 99 | 97 | Size: 1; Name: Pad; Type: pad; R/W: R | O
enum16 | CfgSt |  |  | Name: NOT_CONFIGURED; Label: not configured; Value: 0 |  | the stack is not configured
enum16 | CfgSt |  |  | Name: VALID_SETTING; Label: valid setting; Value: 1 |  | a valid configuration from BOOTP, DHCP, or NV mem
enum16 | CfgSt |  |  | Name: VALID_HW; Label: valid hardware; Value: 2 |  | a valid configuration from hardware settings
bitfield16 | ChgSt |  |  | Name: PENDING; Label: pending; Value: 0 |  | a configuration change is pending
bitfield16 | Cap |  |  | Name: DHCP; Label: DHCP; Value: 1 |  | Use DHCP
bitfield16 | Cap |  |  | Name: BOOTP; Label: BOOTP; Value: 2 |  | Use BOOTP
bitfield16 | Cap |  |  | Name: ZEROCONF; Label: zeroconf; Value: 3 |  | Use Zeroconf
bitfield16 | Cap |  |  | Name: DNS; Label: DNS; Value: 3 |  | DNS Client capable
bitfield16 | Cap |  |  | Name: CFG_SETTABLE; Label: configurable; Value: 4 |  | Settable configuration capable
bitfield16 | Cap |  |  | Name: HW_CONFIG; Label: hw; Value: 5 |  | Hardware configuration capable
bitfield16 | Cap |  |  | Name: NTP_CLIENT; Label: ntp; Value: 6 |  | NTP Client capable
bitfield16 | Cap |  |  | Name: RESET_REQUIRED; Label: reset required; Value: 7 |  | configuration change requires reset
enum16 | Cfg |  |  | Name: STATIC; Label: static; Value: 0 |  | Use static IP
enum16 | Cfg |  |  | Name: DHCP; Label: DHCP; Value: 1 |  | Use DHCP
enum16 | Cfg |  |  | Name: BOOTP; Label: BOOTP; Value: 2 |  | Use BOOTP
enum16 | Cfg |  |  | Name: ZEROCONF; Label: zeroconf; Value: 3 |  | Use Zeroconf
enum16 | Ctl |  |  | Name: ENABLE_DNS; Label: DNS; Value: 0 |  | Enable DNS
enum16 | Ctl |  |  | Name: ENABLE_NTP; Label: NTP; Value: 1 |  | Enable NTP

## 13
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | IPv6 | 13 | uint16 |  |  | R | M | Include to support an IPv6 protocol stack on this interface
Header |  | 1 |  | 1 | L |  | 174 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 4 | Nam | Name |  | string |  |  | RW | O | Interface name
Fixed Block |  | 6 | 4 | 1 | CfgSt | Config Status |  | enum16 |  |  | R | M | Enumerated value. Configuration status
Fixed Block |  | 7 | 5 | 1 | ChgSt | Change Status |  | bitfield16 |  |  | R | M | Bitmask value. A configuration change is pending
Fixed Block |  | 8 | 6 | 1 | Cap | Config Capability |  | bitfield16 |  |  | R | M | Bitmask value. Identify capable sources of configuration
Fixed Block |  | 9 | 7 | 1 | Cfg | IPv6 Config |  | enum16 |  |  | RW | M | Enumerated value. Configuration method used.
Fixed Block |  | 10 | 8 | 1 | Ctl | Control |  | enum16 |  |  | RW | M | Bitmask value. Configure use of services
Fixed Block |  | 11 | 9 | 20 | Addr | IP |  | string |  |  | RW | M | IPv6 numeric address as a dotted string xxxx.xxxx.xxxx.xxxx
Fixed Block |  | 31 | 29 | 20 | CIDR | CIDR |  | string |  |  | RW | O | Classless Inter-Domain Routing Number
Fixed Block |  | 51 | 49 | 20 | Gw | Gateway |  | string |  |  | RW | O | IPv6 numeric address as a dotted string xxxx.xxxx.xxxx.xxxx
Fixed Block |  | 71 | 69 | 20 | DNS1 | DNS1 |  | string |  |  | RW | O | IPv6 numeric DNS address as a dotted string xxxx.xxxx.xxxx.xxxx
Fixed Block |  | 91 | 89 | 20 | DNS2 | DNS2 |  | string |  |  | RW | O | IPv6 numeric DNS address as a dotted string xxxx.xxxx.xxxx.xxxx
Fixed Block |  | 111 | 109 | 20 | NTP1 | NTP1 |  | string |  |  | RW | O | IPv6 numeric NTP address as a name or dotted string xxxx.xxxx.xxxx.xxxx
Fixed Block |  | 131 | 129 | 20 | NTP2 | NTP2 |  | string |  |  | RW | O | IPv6 numeric NTP address as a name or dotted string xxxx.xxxx.xxxx.xxxx
Fixed Block |  | 151 | 149 | 12 | DomNam | Domain |  | string |  |  | RW | O | Domain name (24 chars max)
Fixed Block |  | 163 | 161 | 12 | HostNam | Host Name |  | string |  |  | RW | O | Host name (24 chars max)
Fixed Block |  | 175 | 173 | Size: 1; Name: Pad; Type: pad; R/W: R | O
enum16 | CfgSt |  |  | Name: NOT_CONFIGURED; Label: not configured; Value: 0 |  | the stack is not configured
enum16 | CfgSt |  |  | Name: VALID_SETTING; Label: valid setting; Value: 1 |  | a valid configuration from BOOTP, DHCP, or NV mem
enum16 | CfgSt |  |  | Name: VALID_HW; Label: valid hardware; Value: 2 |  | a valid configuration from hardware settings
bitfield16 | ChgSt |  |  | Name: PENDING; Label: pending; Value: 0 |  | a configuration change is pending
bitfield16 | Cap |  |  | Name: DHCP; Label: DHCP; Value: 1 |  | Use DHCP
bitfield16 | Cap |  |  | Name: BOOTP; Label: BOOTP; Value: 2 |  | Use BOOTP
bitfield16 | Cap |  |  | Name: ZEROCONF; Label: zeroconf; Value: 3 |  | Use Zeroconf
bitfield16 | Cap |  |  | Name: DNS; Label: DNS; Value: 3 |  | DNS Client capable
bitfield16 | Cap |  |  | Name: CFG_SETTABLE; Label: configurable; Value: 4 |  | Settable configuration capable
bitfield16 | Cap |  |  | Name: HW_CONFIG; Label: hw; Value: 5 |  | Hardware configuration capable
bitfield16 | Cap |  |  | Name: NTP_CLIENT; Label: ntp; Value: 6 |  | NTP Client capable
bitfield16 | Cap |  |  | Name: RESET_REQUIRED; Label: reset required; Value: 7 |  | configuration change requires reset
enum16 | Cfg |  |  | Name: STATIC; Label: static; Value: 0 |  | Use static IP
enum16 | Cfg |  |  | Name: DHCP; Label: DHCP; Value: 1 |  | Use DHCP
enum16 | Cfg |  |  | Name: BOOTP; Label: BOOTP; Value: 2 |  | Use BOOTP
enum16 | Cfg |  |  | Name: ZEROCONF; Label: zeroconf; Value: 3 |  | Use Zeroconf
enum16 | Ctl |  |  | Name: ENABLE_DNS; Label: DNS; Value: 0 |  | Enable DNS
enum16 | Ctl |  |  | Name: ENABLE_NTP; Label: NTP; Value: 1 |  | Enable NTP

## 14
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Proxy Server | 14 | uint16 |  |  | R | M | Include this block to allow for a proxy server
Header |  | 1 |  | 1 | L |  | 52 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 4 | Nam | name |  | string |  |  | RW | O | Interface name (8 chars)
Fixed Block |  | 6 | 4 | 1 | Cap | Capabilities |  | bitfield16 |  |  | RW | M | Bitmask value. Proxy configuration capabilites
Fixed Block |  | 7 | 5 | 1 | Cfg | Config |  | enum16 |  |  | RW | M | Enumerated value. Set proxy address type
Fixed Block |  | 8 | 6 | 1 | Typ | Type |  | bitfield16 |  |  | RW | M | Enumerate value. Proxy server type
Fixed Block |  | 9 | 7 | 20 | Addr | Address |  | string |  |  | RW | M | IPv4 or IPv6 proxy hostname or dotteed address (40 chars)
Fixed Block |  | 29 | 27 | 1 | Port | Port |  | uint16 |  |  | RW | M | Proxy port number
Fixed Block |  | 30 | 28 | 12 | User | Username |  | string |  |  | RW | O | Proxy user name
Fixed Block |  | 42 | 40 | 12 | Pw | Password |  | string |  |  | RW | O | Proxy password
bitfield16 | Cap |  |  | Name: NO_PROXY; Label: No Proxy; Value: 0 |  | Turn off the proxy
bitfield16 | Cap |  |  | Name: IPV4_PROXY; Label: IPv4 Proxy; Value: 1 |  | Can proxy IPv4
bitfield16 | Cap |  |  | Name: IPV6_PROXY; Label: IPv6 Proxy; Value: 2 |  | Can proxy IPv6

## 15
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Interface Counters Model | 15 | uint16 |  |  | R | M | Interface counters
Header |  | 1 |  | 1 | L |  | 24 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | Clr | Clear |  | uint16 |  |  | RW | O | Write a "1" to clear all counters
Fixed Block |  | 3 | 1 | 2 | InCnt | Input Count |  | acc32 |  |  | R | O | Number of bytes received
Fixed Block |  | 5 | 3 | 2 | InUcCnt | Input Unicast Count |  | acc32 |  |  | R | O | Number of Unicast packets received
Fixed Block |  | 7 | 5 | 2 | InNUcCnt | Input Non-Unicast Count |  | acc32 |  |  | R | O | Number of non-Unicast packets received
Fixed Block |  | 9 | 7 | 2 | InDscCnt | Input Discarded Count |  | acc32 |  |  | R | O | Number of inbound packets received on the interface but discarded
Fixed Block |  | 11 | 9 | 2 | InErrCnt | Input Error Count |  | acc32 |  |  | R | O | Number of inbound packets that contain errors (excluding discards)
Fixed Block |  | 13 | 11 | 2 | InUnkCnt | Input Unknown Count |  | acc32 |  |  | R | O | Number of inbound packets with unknown protocol
Fixed Block |  | 15 | 13 | 2 | OutCnt | Output Count |  | acc32 |  |  | R | O | Total number of bytes transmitted on this interface
Fixed Block |  | 17 | 15 | 2 | OutUcCnt | Output Unicast Count |  | acc32 |  |  | R | O | Number of Unicast packets transmitted
Fixed Block |  | 19 | 17 | 2 | OutNUcCnt | Output Non-Unicast Count |  | acc32 |  |  | R | O | Number of Non-Unicast packets transmitted
Fixed Block |  | 21 | 19 | 2 | OutDscCnt | Output Discarded Count |  | acc32 |  |  | R | O | Number of Discarded output packets
Fixed Block |  | 23 | 21 | 2 | OutErrCnt | Output Error Count |  | acc32 |  |  | R | O | Number of outbound error packets
Fixed Block |  | 25 | 23 | Size: 1; Name: Pad; Type: pad; R/W: R | O

## 16
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Simple IP Network | 16 | uint16 |  |  | R | M | Include this model for a simple IPv4 network stack
Header |  | 1 |  | 1 | L |  | 52 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 4 | Nam | Name |  | string |  |  | RW | O | Interface name. (8 chars)
Fixed Block |  | 6 | 4 | 1 | Cfg | Config |  | enum16 |  |  | R | M | Enumerated value. Force IPv4 configuration method
Fixed Block |  | 7 | 5 | 1 | Ctl | Control |  | enum16 |  |  | RW | M | Bitmask value Configure use of services
Fixed Block |  | 8 | 6 | 8 | Addr | Address |  | string |  |  | RW | M | IP addreess
Fixed Block |  | 16 | 14 | 8 | Msk | Netmask |  | string |  |  | RW | M | Netmask
Fixed Block |  | 24 | 22 | 8 | Gw | Gateway |  | string |  |  | RW | O | Gateway IP address
Fixed Block |  | 32 | 30 | 8 | DNS1 | DNS1 |  | string |  |  | RW | O | 32 bit IP address of DNS server
Fixed Block |  | 40 | 38 | 8 | DNS2 | DNS2 |  | string |  |  | RW | O | 32 bit IP address of DNS server
Fixed Block |  | 48 | 46 | 4 | MAC | MAC |  | uint64 |  |  | R | O | IEEE MAC address of this interface
Fixed Block |  | 52 | 50 | 1 | LnkCtl | Link Control |  | bitfield16 |  |  | RW | O | Bitmask value. Link control flags
Fixed Block |  | 53 | 51 | Size: 1; Name: Pad; Type: pad; R/W: R | O
enum16 | Cfg |  |  | Name: STATIC; Label: static; Value: 0 |  | A static IP address is assigned
enum16 | Cfg |  |  | Name: DHCP; Label: DHCP; Value: 1 |  | Use DHCP to acquire an IP address
enum16 | Ctl |  |  | Name: ENABLE_DNS; Label: DNS; Value: 0 |  | Enable DNS use
enum16 | Ctl |  |  | Name: ENABLE_NTP; Label: NTP; Value: 1 |  | Enable NTP use
bitfield16 | LnkCtl |  |  | Name: AUTONEGOTIATE; Label: auto-negotiate; Value: 0 |  | Enable auto-negotiation
bitfield16 | LnkCtl |  |  | Name: FULL_DUPLEX; Label: full duplex; Value: 1 |  | Force full duplex operation
bitfield16 | LnkCtl |  |  | Name: FORCE_10MB; Label: 10Mbs; Value: 2 |  | Force 10 Mb/s link speed
bitfield16 | LnkCtl |  |  | Name: FORCE_100MB; Label: 100Mbs; Value: 3 |  | Force 100 Mb/s link speed
bitfield16 | LnkCtl |  |  | Name: FORCE_1GB; Label: 1Gbs; Value: 3 |  | Force 1 Gb/s link speed

## 17
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Serial Interface | 17 | uint16 |  |  | R | M | Include this model for serial interface configuration support
Header |  | 1 |  | 1 | L |  | 12 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 4 | Nam | Name |  | string |  |  | RW | O | Interface name (8 chars)
Fixed Block |  | 6 | 4 | 2 | Rte | Rate |  | uint32 | bps |  | RW | M | Interface baud rate in bits per second
Fixed Block |  | 8 | 6 | 1 | Bits | Bits |  | uint16 |  |  | RW | M | Number of data bits per character
Fixed Block |  | 9 | 7 | 1 | Pty | Parity |  | enum16 |  |  | RW | M | Bitmask value. Parity setting
Fixed Block |  | 10 | 8 | 1 | Dup | Duplex |  | enum16 |  |  | RW | O | Enumerated value. Duplex mode
Fixed Block |  | 11 | 9 | 1 | Flw | Flow Control |  | enum16 |  |  | RW | O | Flow Control Method
Fixed Block |  | 12 | 10 | 1 | Typ | Interface Type |  | enum16 |  |  | R | O | Enumerated value. Interface type
Fixed Block |  | 13 | 11 | 1 | Pcol | Protocol |  | enum16 |  |  | R | O | Enumerated value. Serial protocol selection
enum16 | Pty |  |  | Name: NONE; Label: none; Value: 0 |  | No flow control
enum16 | Pty |  |  | Name: ODD; Label: odd; Value: 1 |  | Odd Parity
enum16 | Pty |  |  | Name: EVEN; Label: even; Value: 2 |  | Even Parity
enum16 | Dup |  |  | Name: FULL; Label: full; Value: 0 |  | Full Duplex
enum16 | Dup |  |  | Name: HALF; Label: half; Value: 1 |  | Half Duplex
enum16 | Flw |  |  | Name: NONE; Label: none; Value: 0 |  | No flow control
enum16 | Flw |  |  | Name: HW; Label: hardware; Value: 1 |  | Hardware flow control
enum16 | Flw |  |  | Name: XONXOFF; Label: software; Value: 2 |  | Soft (XON/XOFF) flow control
enum16 | Typ |  |  | Name: UNKNOWN; Label: unknown; Value: 0 |  | Unknown protocol
enum16 | Typ |  |  | Name: RS232; Label: RS232; Value: 1 |  | RS232 interface type
enum16 | Typ |  |  | Name: RS485; Label: RS485; Value: 2 |  | RS485 interface type
enum16 | Pcol |  |  | Name: UNKNOWN; Label: unknown; Value: 0 |  | Unknown protocol
enum16 | Pcol |  |  | Name: MODBUS; Label: Modbus; Value: 1 |  | Modbus protocol
enum16 | Pcol |  |  | Name: VENDOR; Label: vendor specific; Value: 2

## 18
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Cellular Link | 18 | uint16 |  |  | R | M | Include this model to support a cellular interface link
Header |  | 1 |  | 1 | L |  | 22 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 4 | Nam | Name |  | string |  |  | RW | O | Interface name
Fixed Block |  | 6 | 4 | 2 | IMEI | IMEI |  | uint32 |  |  | RW | O | International Mobile Equipment Identifier for the interface
Fixed Block |  | 8 | 6 | 4 | APN | APN |  | string |  |  | RW | O | Access Point Name for the interface
Fixed Block |  | 12 | 10 | 6 | Num | Number |  | string |  |  | RW | O | Phone number for the interface
Fixed Block |  | 18 | 16 | 6 | Pin | PIN |  | string |  |  | RW | O | Personal Identification Number for the interface

## 19
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | PPP Link | 19 | uint16 |  |  | R | M | Include this model to configure a Point-to-Point Protocol link
Header |  | 1 |  | 1 | L |  | 30 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 4 | Nam | Name |  | string |  |  | RW | O | Interface name
Fixed Block |  | 6 | 4 | 2 | Rte | Rate |  | uint32 | bps |  | RW | M | Interface baud rate in bits per second
Fixed Block |  | 8 | 6 | 1 | Bits | Bits |  | uint16 |  |  | RW | M | Number of data bits per character
Fixed Block |  | 9 | 7 | 1 | Pty | Parity |  | enum16 |  |  | RW | M | Bitmask value. Parity setting
Fixed Block |  | 10 | 8 | 1 | Dup | Duplex |  | enum16 |  |  | RW | O | Enumerated value. Duplex mode
Fixed Block |  | 11 | 9 | 1 | Flw | Flow Control |  | enum16 |  |  | RW | O | Flow Control Method
Fixed Block |  | 12 | 10 | 1 | Auth | Authentication |  | enum16 |  |  | R | O | Enumerated value. Authentication method
Fixed Block |  | 13 | 11 | 12 | UsrNam | Username |  | string |  |  | R | O | Username for authentication
Fixed Block |  | 25 | 23 | 6 | Pw | Password |  | string |  |  | R | O | Password for authentication
Fixed Block |  | 31 | 29 | Size: 1; Name: Pad; Type: pad; R/W: R | O
enum16 | Pty |  |  | Name: NONE; Label: none; Value: 0 |  | No Authentication
enum16 | Pty |  |  | Name: ODD; Label: odd; Value: 1 |  | Odd Parity
enum16 | Pty |  |  | Name: EVEN; Label: even; Value: 2 |  | Even Parity
enum16 | Dup |  |  | Name: FULL; Label: full; Value: 0 |  | Full Duplex
enum16 | Dup |  |  | Name: HALF; Label: half; Value: 1 |  | Half Duplex
enum16 | Flw |  |  | Name: NONE; Label: none; Value: 0 |  | No Authentication
enum16 | Flw |  |  | Name: HW; Label: hardware; Value: 1 |  | Hardware flow control
enum16 | Flw |  |  | Name: XONXOFF; Label: software; Value: 2 |  | Soft (XON/XOFF) flow control
enum16 | Auth |  |  | Name: NONE; Label: none; Value: 0 |  | No Authentication
enum16 | Auth |  |  | Name: PAP; Label: PAP; Value: 1 |  | Use PAP authentication
enum16 | Auth |  |  | Name: CHAP; Label: CHAP; Value: 2 |  | Use CHAP authentication

## 101
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Inverter (Single Phase) | 101 | uint16 |  |  | R | M | Include this model for single phase inverter monitoring
Header |  | 1 |  | 1 | L |  | 50 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | A | Amps |  | uint16 | A | A_SF | R | M | AC Current
Fixed Block |  | 3 | 1 | 1 | AphA | Amps PhaseA |  | uint16 | A | A_SF | R | M | Phase A Current | Connected Phase
Fixed Block |  | 4 | 2 | 1 | AphB | Amps PhaseB |  | uint16 | A | A_SF | R | O | Phase B Current
Fixed Block |  | 5 | 3 | 1 | AphC | Amps PhaseC |  | uint16 | A | A_SF | R | O | Phase C Current
Fixed Block |  | 6 | 4 | Size: 1; Name: A_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 7 | 5 | 1 | PPVphAB | Phase Voltage AB |  | uint16 | V | V_SF | R | O | Phase Voltage AB
Fixed Block |  | 8 | 6 | 1 | PPVphBC | Phase Voltage BC |  | uint16 | V | V_SF | R | O | Phase Voltage BC
Fixed Block |  | 9 | 7 | 1 | PPVphCA | Phase Voltage CA |  | uint16 | V | V_SF | R | O | Phase Voltage CA
Fixed Block |  | 10 | 8 | 1 | PhVphA | Phase Voltage AN |  | uint16 | V | V_SF | R | M | Phase Voltage AN
Fixed Block |  | 11 | 9 | 1 | PhVphB | Phase Voltage BN |  | uint16 | V | V_SF | R | O | Phase Voltage BN
Fixed Block |  | 12 | 10 | 1 | PhVphC | Phase Voltage CN |  | uint16 | V | V_SF | R | O | Phase Voltage CN
Fixed Block |  | 13 | 11 | Size: 1; Name: V_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 14 | 12 | 1 | W | Watts |  | int16 | W | W_SF | R | M | AC Power
Fixed Block |  | 15 | 13 | Size: 1; Name: W_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 16 | 14 | 1 | Hz | Hz |  | uint16 | Hz | Hz_SF | R | M | Line Frequency
Fixed Block |  | 17 | 15 | Size: 1; Name: Hz_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 18 | 16 | 1 | VA | VA |  | int16 | VA | VA_SF | R | O | AC Apparent Power
Fixed Block |  | 19 | 17 | Size: 1; Name: VA_SF; Type: sunssf; R/W: R | O
Fixed Block |  | 20 | 18 | 1 | VAr | VAr |  | int16 | var | VAr_SF | R | O | AC Reactive Power
Fixed Block |  | 21 | 19 | Size: 1; Name: VAr_SF; Type: sunssf; R/W: R | O
Fixed Block |  | 22 | 20 | 1 | PF | PF |  | int16 | Pct | PF_SF | R | O | AC Power Factor
Fixed Block |  | 23 | 21 | Size: 1; Name: PF_SF; Type: sunssf; R/W: R | O
Fixed Block |  | 24 | 22 | 2 | WH | WattHours |  | acc32 | Wh | WH_SF | R | M | AC Energy
Fixed Block |  | 26 | 24 | Size: 1; Name: WH_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 27 | 25 | 1 | DCA | DC Amps |  | uint16 | A | DCA_SF | R | O | DC Current
Fixed Block |  | 28 | 26 | Size: 1; Name: DCA_SF; Type: sunssf; R/W: R | O
Fixed Block |  | 29 | 27 | 1 | DCV | DC Voltage |  | uint16 | V | DCV_SF | R | O | DC Voltage
Fixed Block |  | 30 | 28 | Size: 1; Name: DCV_SF; Type: sunssf; R/W: R | O
Fixed Block |  | 31 | 29 | 1 | DCW | DC Watts |  | int16 | W | DCW_SF | R | O | DC Power
Fixed Block |  | 32 | 30 | Size: 1; Name: DCW_SF; Type: sunssf; R/W: R | O
Fixed Block |  | 33 | 31 | 1 | TmpCab | Cabinet Temperature |  | int16 | C | Tmp_SF | R | M | Cabinet Temperature
Fixed Block |  | 34 | 32 | 1 | TmpSnk | Heat Sink Temperature |  | int16 | C | Tmp_SF | R | O | Heat Sink Temperature
Fixed Block |  | 35 | 33 | 1 | TmpTrns | Transformer Temperature |  | int16 | C | Tmp_SF | R | O | Transformer Temperature
Fixed Block |  | 36 | 34 | 1 | TmpOt | Other Temperature |  | int16 | C | Tmp_SF | R | O | Other Temperature
Fixed Block |  | 37 | 35 | Size: 1; Name: Tmp_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 38 | 36 | 1 | St | Operating State |  | enum16 |  |  | R | M | Enumerated value. Operating state
Fixed Block |  | 39 | 37 | 1 | StVnd | Vendor Operating State |  | enum16 |  |  | R | O | Vendor specific operating state code
Fixed Block |  | 40 | 38 | 2 | Evt1 | Event1 |  | bitfield32 |  |  | R | M | Bitmask value. Event fields
Fixed Block |  | 42 | 40 | 2 | Evt2 | Event Bitfield 2 |  | bitfield32 |  |  | R | M | Reserved for future use
Fixed Block |  | 44 | 42 | 2 | EvtVnd1 | Vendor Event Bitfield 1 |  | bitfield32 |  |  | R | O | Vendor defined events
Fixed Block |  | 46 | 44 | 2 | EvtVnd2 | Vendor Event Bitfield 2 |  | bitfield32 |  |  | R | O | Vendor defined events
Fixed Block |  | 48 | 46 | 2 | EvtVnd3 | Vendor Event Bitfield 3 |  | bitfield32 |  |  | R | O | Vendor defined events
Fixed Block |  | 50 | 48 | 2 | EvtVnd4 | Vendor Event Bitfield 4 |  | bitfield32 |  |  | R | O | Vendor defined events
enum16 | St |  |  | Name: OFF; Label: Off; Value: 1 |  | Device is not operating
enum16 | St |  |  | Name: SLEEPING; Label: Sleeping; Value: 2 |  | Device is sleeping / auto-shudown
enum16 | St |  |  | Name: STARTING; Label: Starting; Value: 3 |  | Device is staring up
enum16 | St |  |  | Name: MPPT; Label: MPPT; Value: 4 |  | Device is auto tracking maximum power point
enum16 | St |  |  | Name: THROTTLED; Label: Throttled; Value: 5 |  | Device is operating at reduced power output
enum16 | St |  |  | Name: SHUTTING_DOWN; Label: Shutting down; Value: 6 |  | Device is shutting down
enum16 | St |  |  | Name: FAULT; Label: Fault; Value: 7 |  | One or more faults exist
enum16 | St |  |  | Name: STANDBY; Label: Standby; Value: 8 |  | Device is in standby mode
bitfield32 | Evt1 |  |  | Name: GROUND_FAULT; Label: Ground fault; Value: 0
bitfield32 | Evt1 |  |  | Name: DC_OVER_VOLT; Label: DC over voltage; Value: 1
bitfield32 | Evt1 |  |  | Name: AC_DISCONNECT; Label: AC disconnect open; Value: 2
bitfield32 | Evt1 |  |  | Name: DC_DISCONNECT; Label: DC disconnect open; Value: 3
bitfield32 | Evt1 |  |  | Name: GRID_DISCONNECT; Label: Grid disconnect; Value: 4
bitfield32 | Evt1 |  |  | Name: CABINET_OPEN; Label: Cabinet open; Value: 5
bitfield32 | Evt1 |  |  | Name: MANUAL_SHUTDOWN; Label: Manual shutdown; Value: 6
bitfield32 | Evt1 |  |  | Name: OVER_TEMP; Label: Over temperature; Value: 7
bitfield32 | Evt1 |  |  | Name: OVER_FREQUENCY; Label: Frequency above limit; Value: 8
bitfield32 | Evt1 |  |  | Name: UNDER_FREQUENCY; Label: Frequency under limit; Value: 9
bitfield32 | Evt1 |  |  | Name: AC_OVER_VOLT; Label: AC Voltage above limit; Value: 10
bitfield32 | Evt1 |  |  | Name: AC_UNDER_VOLT; Label: AC Voltage under limit; Value: 11
bitfield32 | Evt1 |  |  | Name: BLOWN_STRING_FUSE; Label: Blown String fuse on input; Value: 12
bitfield32 | Evt1 |  |  | Name: UNDER_TEMP; Label: Under temperature; Value: 13
bitfield32 | Evt1 |  |  | Name: MEMORY_LOSS; Label: Generic Memory or Communication error (internal); Value: 14
bitfield32 | Evt1 |  |  | Name: HW_TEST_FAILURE; Label: Hardware test failure; Value: 15

## 102
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Inverter (Split-Phase) | 102 | uint16 |  |  | R | M | Include this model for split phase inverter monitoring
Header |  | 1 |  | 1 | L |  | 50 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | A | Amps |  | uint16 | A | A_SF | R | M | AC Current | Sum of active phases
Fixed Block |  | 3 | 1 | 1 | AphA | Amps PhaseA |  | uint16 | A | A_SF | R | M | Phase A Current | Connected Phase
Fixed Block |  | 4 | 2 | 1 | AphB | Amps PhaseB |  | uint16 | A | A_SF | R | M | Phase B Current | Connected Phase
Fixed Block |  | 5 | 3 | 1 | AphC | Amps PhaseC |  | uint16 | A | A_SF | R | O | Phase C Current
Fixed Block |  | 6 | 4 | Size: 1; Name: A_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 7 | 5 | 1 | PPVphAB | Phase Voltage AB |  | uint16 | V | V_SF | R | O | Phase Voltage AB
Fixed Block |  | 8 | 6 | 1 | PPVphBC | Phase Voltage BC |  | uint16 | V | V_SF | R | O | Phase Voltage BC
Fixed Block |  | 9 | 7 | 1 | PPVphCA | Phase Voltage CA |  | uint16 | V | V_SF | R | O | Phase Voltage CA
Fixed Block |  | 10 | 8 | 1 | PhVphA | Phase Voltage AN |  | uint16 | V | V_SF | R | M | Phase Voltage AN
Fixed Block |  | 11 | 9 | 1 | PhVphB | Phase Voltage BN |  | uint16 | V | V_SF | R | M | Phase Voltage BN
Fixed Block |  | 12 | 10 | 1 | PhVphC | Phase Voltage CN |  | uint16 | V | V_SF | R | O | Phase Voltage CN
Fixed Block |  | 13 | 11 | Size: 1; Name: V_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 14 | 12 | 1 | W | Watts |  | int16 | W | W_SF | R | M | AC Power
Fixed Block |  | 15 | 13 | Size: 1; Name: W_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 16 | 14 | 1 | Hz | Hz |  | uint16 | Hz | Hz_SF | R | M | Line Frequency
Fixed Block |  | 17 | 15 | Size: 1; Name: Hz_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 18 | 16 | 1 | VA | VA |  | int16 | VA | VA_SF | R | O | AC Apparent Power
Fixed Block |  | 19 | 17 | Size: 1; Name: VA_SF; Type: sunssf; R/W: R | O
Fixed Block |  | 20 | 18 | 1 | VAr | VAr |  | int16 | var | VAr_SF | R | O | AC Reactive Power
Fixed Block |  | 21 | 19 | Size: 1; Name: VAr_SF; Type: sunssf; R/W: R | O
Fixed Block |  | 22 | 20 | 1 | PF | PF |  | int16 | Pct | PF_SF | R | O | AC Power Factor
Fixed Block |  | 23 | 21 | Size: 1; Name: PF_SF; Type: sunssf; R/W: R | O
Fixed Block |  | 24 | 22 | 2 | WH | WattHours |  | acc32 | Wh | WH_SF | R | M | AC Energy
Fixed Block |  | 26 | 24 | Size: 1; Name: WH_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 27 | 25 | 1 | DCA | DC Amps |  | uint16 | A | DCA_SF | R | O | DC Current
Fixed Block |  | 28 | 26 | Size: 1; Name: DCA_SF; Type: sunssf; R/W: R | O
Fixed Block |  | 29 | 27 | 1 | DCV | DC Voltage |  | uint16 | V | DCV_SF | R | O | DC Voltage
Fixed Block |  | 30 | 28 | Size: 1; Name: DCV_SF; Type: sunssf; R/W: R | O
Fixed Block |  | 31 | 29 | 1 | DCW | DC Watts |  | int16 | W | DCW_SF | R | O | DC Power
Fixed Block |  | 32 | 30 | Size: 1; Name: DCW_SF; Type: sunssf; R/W: R | O
Fixed Block |  | 33 | 31 | 1 | TmpCab | Cabinet Temperature |  | int16 | C | Tmp_SF | R | M | Cabinet Temperature
Fixed Block |  | 34 | 32 | 1 | TmpSnk | Heat Sink Temperature |  | int16 | C | Tmp_SF | R | O | Heat Sink Temperature
Fixed Block |  | 35 | 33 | 1 | TmpTrns | Transformer Temperature |  | int16 | C | Tmp_SF | R | O | Transformer Temperature
Fixed Block |  | 36 | 34 | 1 | TmpOt | Other Temperature |  | int16 | C | Tmp_SF | R | O | Other Temperature
Fixed Block |  | 37 | 35 | Size: 1; Name: Tmp_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 38 | 36 | 1 | St | Operating State |  | enum16 |  |  | R | M | Enumerated value. Operating state
Fixed Block |  | 39 | 37 | 1 | StVnd | Vendor Operating State |  | enum16 |  |  | R | O | Vendor specific operating state code
Fixed Block |  | 40 | 38 | 2 | Evt1 | Event1 |  | bitfield32 |  |  | R | M | Bitmask value. Event fields
Fixed Block |  | 42 | 40 | 2 | Evt2 | Event Bitfield 2 |  | bitfield32 |  |  | R | M | Reserved for future use
Fixed Block |  | 44 | 42 | 2 | EvtVnd1 | Vendor Event Bitfield 1 |  | bitfield32 |  |  | R | O | Vendor defined events
Fixed Block |  | 46 | 44 | 2 | EvtVnd2 | Vendor Event Bitfield 2 |  | bitfield32 |  |  | R | O | Vendor defined events
Fixed Block |  | 48 | 46 | 2 | EvtVnd3 | Vendor Event Bitfield 3 |  | bitfield32 |  |  | R | O | Vendor defined events
Fixed Block |  | 50 | 48 | 2 | EvtVnd4 | Vendor Event Bitfield 4 |  | bitfield32 |  |  | R | O | Vendor defined events
enum16 | St |  |  | Name: OFF; Label: Off; Value: 1 |  | Device is not operating
enum16 | St |  |  | Name: SLEEPING; Label: Sleeping; Value: 2 |  | Device is sleeping / auto-shudown
enum16 | St |  |  | Name: STARTING; Label: Starting; Value: 3 |  | Device is staring up
enum16 | St |  |  | Name: MPPT; Label: MPPT; Value: 4 |  | Device is auto tracking maximum power point
enum16 | St |  |  | Name: THROTTLED; Label: Throttled; Value: 5 |  | Device is operating at reduced power output
enum16 | St |  |  | Name: SHUTTING_DOWN; Label: Shutting down; Value: 6 |  | Device is shutting down
enum16 | St |  |  | Name: FAULT; Label: Fault; Value: 7 |  | One or more faults exist
enum16 | St |  |  | Name: STANDBY; Label: Standby; Value: 8 |  | Device is in standby mode
bitfield32 | Evt1 |  |  | Name: GROUND_FAULT; Label: Ground fault; Value: 0
bitfield32 | Evt1 |  |  | Name: DC_OVER_VOLT; Label: DC over voltage; Value: 1
bitfield32 | Evt1 |  |  | Name: AC_DISCONNECT; Label: AC disconnect open; Value: 2
bitfield32 | Evt1 |  |  | Name: DC_DISCONNECT; Label: DC disconnect open; Value: 3
bitfield32 | Evt1 |  |  | Name: GRID_DISCONNECT; Label: Grid shutdown; Value: 4
bitfield32 | Evt1 |  |  | Name: CABINET_OPEN; Label: Cabinet open; Value: 5
bitfield32 | Evt1 |  |  | Name: MANUAL_SHUTDOWN; Label: Manual shutdown; Value: 6
bitfield32 | Evt1 |  |  | Name: OVER_TEMP; Label: Over temperature; Value: 7
bitfield32 | Evt1 |  |  | Name: OVER_FREQUENCY; Label: Frequency above limit; Value: 8
bitfield32 | Evt1 |  |  | Name: UNDER_FREQUENCY; Label: Frequency under limit; Value: 9
bitfield32 | Evt1 |  |  | Name: AC_OVER_VOLT; Label: AC Voltage above limit; Value: 10
bitfield32 | Evt1 |  |  | Name: AC_UNDER_VOLT; Label: AC Voltage under limit; Value: 11
bitfield32 | Evt1 |  |  | Name: BLOWN_STRING_FUSE; Label: Blown String fuse on input; Value: 12
bitfield32 | Evt1 |  |  | Name: UNDER_TEMP; Label: Under temperature; Value: 13
bitfield32 | Evt1 |  |  | Name: MEMORY_LOSS; Label: Generic Memory or Communication error (internal); Value: 14
bitfield32 | Evt1 |  |  | Name: HW_TEST_FAILURE; Label: Hardware test failure; Value: 15

## 103
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Inverter (Three Phase) | 103 | uint16 |  |  | R | M | Include this model for three phase inverter monitoring
Header |  | 1 |  | 1 | L |  | 50 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | A | Amps |  | uint16 | A | A_SF | R | M | AC Current | Sum of active phases
Fixed Block |  | 3 | 1 | 1 | AphA | Amps PhaseA |  | uint16 | A | A_SF | R | M | Phase A Current | Connected Phase
Fixed Block |  | 4 | 2 | 1 | AphB | Amps PhaseB |  | uint16 | A | A_SF | R | M | Phase B Current | Connected Phase
Fixed Block |  | 5 | 3 | 1 | AphC | Amps PhaseC |  | uint16 | A | A_SF | R | M | Phase C Current | Connected Phase
Fixed Block |  | 6 | 4 | Size: 1; Name: A_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 7 | 5 | 1 | PPVphAB | Phase Voltage AB |  | uint16 | V | V_SF | R | O | Phase Voltage AB
Fixed Block |  | 8 | 6 | 1 | PPVphBC | Phase Voltage BC |  | uint16 | V | V_SF | R | O | Phase Voltage BC
Fixed Block |  | 9 | 7 | 1 | PPVphCA | Phase Voltage CA |  | uint16 | V | V_SF | R | O | Phase Voltage CA
Fixed Block |  | 10 | 8 | 1 | PhVphA | Phase Voltage AN |  | uint16 | V | V_SF | R | M | Phase Voltage AN
Fixed Block |  | 11 | 9 | 1 | PhVphB | Phase Voltage BN |  | uint16 | V | V_SF | R | M | Phase Voltage BN
Fixed Block |  | 12 | 10 | 1 | PhVphC | Phase Voltage CN |  | uint16 | V | V_SF | R | M | Phase Voltage CN
Fixed Block |  | 13 | 11 | Size: 1; Name: V_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 14 | 12 | 1 | W | Watts |  | int16 | W | W_SF | R | M | AC Power
Fixed Block |  | 15 | 13 | Size: 1; Name: W_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 16 | 14 | 1 | Hz | Hz |  | uint16 | Hz | Hz_SF | R | M | Line Frequency
Fixed Block |  | 17 | 15 | Size: 1; Name: Hz_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 18 | 16 | 1 | VA | VA |  | int16 | VA | VA_SF | R | O | AC Apparent Power
Fixed Block |  | 19 | 17 | Size: 1; Name: VA_SF; Type: sunssf; R/W: R | O
Fixed Block |  | 20 | 18 | 1 | VAr | VAr |  | int16 | var | VAr_SF | R | O | AC Reactive Power
Fixed Block |  | 21 | 19 | Size: 1; Name: VAr_SF; Type: sunssf; R/W: R | O
Fixed Block |  | 22 | 20 | 1 | PF | PF |  | int16 | Pct | PF_SF | R | O | AC Power Factor
Fixed Block |  | 23 | 21 | Size: 1; Name: PF_SF; Type: sunssf; R/W: R | O
Fixed Block |  | 24 | 22 | 2 | WH | WattHours |  | acc32 | Wh | WH_SF | R | M | AC Energy
Fixed Block |  | 26 | 24 | Size: 1; Name: WH_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 27 | 25 | 1 | DCA | DC Amps |  | uint16 | A | DCA_SF | R | O | DC Current
Fixed Block |  | 28 | 26 | Size: 1; Name: DCA_SF; Type: sunssf; R/W: R | O
Fixed Block |  | 29 | 27 | 1 | DCV | DC Voltage |  | uint16 | V | DCV_SF | R | O | DC Voltage
Fixed Block |  | 30 | 28 | Size: 1; Name: DCV_SF; Type: sunssf; R/W: R | O
Fixed Block |  | 31 | 29 | 1 | DCW | DC Watts |  | int16 | W | DCW_SF | R | O | DC Power
Fixed Block |  | 32 | 30 | Size: 1; Name: DCW_SF; Type: sunssf; R/W: R | O
Fixed Block |  | 33 | 31 | 1 | TmpCab | Cabinet Temperature |  | int16 | C | Tmp_SF | R | M | Cabinet Temperature
Fixed Block |  | 34 | 32 | 1 | TmpSnk | Heat Sink Temperature |  | int16 | C | Tmp_SF | R | O | Heat Sink Temperature
Fixed Block |  | 35 | 33 | 1 | TmpTrns | Transformer Temperature |  | int16 | C | Tmp_SF | R | O | Transformer Temperature
Fixed Block |  | 36 | 34 | 1 | TmpOt | Other Temperature |  | int16 | C | Tmp_SF | R | O | Other Temperature
Fixed Block |  | 37 | 35 | Size: 1; Name: Tmp_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 38 | 36 | 1 | St | Operating State |  | enum16 |  |  | R | M | Enumerated value. Operating state
Fixed Block |  | 39 | 37 | 1 | StVnd | Vendor Operating State |  | enum16 |  |  | R | O | Vendor specific operating state code
Fixed Block |  | 40 | 38 | 2 | Evt1 | Event1 |  | bitfield32 |  |  | R | M | Bitmask value. Event fields
Fixed Block |  | 42 | 40 | 2 | Evt2 | Event Bitfield 2 |  | bitfield32 |  |  | R | M | Reserved for future use
Fixed Block |  | 44 | 42 | 2 | EvtVnd1 | Vendor Event Bitfield 1 |  | bitfield32 |  |  | R | O | Vendor defined events
Fixed Block |  | 46 | 44 | 2 | EvtVnd2 | Vendor Event Bitfield 2 |  | bitfield32 |  |  | R | O | Vendor defined events
Fixed Block |  | 48 | 46 | 2 | EvtVnd3 | Vendor Event Bitfield 3 |  | bitfield32 |  |  | R | O | Vendor defined events
Fixed Block |  | 50 | 48 | 2 | EvtVnd4 | Vendor Event Bitfield 4 |  | bitfield32 |  |  | R | O | Vendor defined events
enum16 | St |  |  | Name: OFF; Label: Off; Value: 1 |  | Device is not operating
enum16 | St |  |  | Name: SLEEPING; Label: Sleeping; Value: 2 |  | Device is sleeping / auto-shudown
enum16 | St |  |  | Name: STARTING; Label: Starting; Value: 3 |  | Device is staring up
enum16 | St |  |  | Name: MPPT; Label: MPPT; Value: 4 |  | Device is auto tracking maximum power point
enum16 | St |  |  | Name: THROTTLED; Label: Throttled; Value: 5 |  | Device is operating at reduced power output
enum16 | St |  |  | Name: SHUTTING_DOWN; Label: Shutting down; Value: 6 |  | Device is shutting down
enum16 | St |  |  | Name: FAULT; Label: Fault; Value: 7 |  | One or more faults exist
enum16 | St |  |  | Name: STANDBY; Label: Standby; Value: 8 |  | Device is in standby mode
bitfield32 | Evt1 |  |  | Name: GROUND_FAULT; Label: Ground fault; Value: 0
bitfield32 | Evt1 |  |  | Name: DC_OVER_VOLT; Label: DC over voltage; Value: 1
bitfield32 | Evt1 |  |  | Name: AC_DISCONNECT; Label: AC disconnect open; Value: 2
bitfield32 | Evt1 |  |  | Name: DC_DISCONNECT; Label: DC disconnect open; Value: 3
bitfield32 | Evt1 |  |  | Name: GRID_DISCONNECT; Label: Grid shutdown; Value: 4
bitfield32 | Evt1 |  |  | Name: CABINET_OPEN; Label: Cabinet open; Value: 5
bitfield32 | Evt1 |  |  | Name: MANUAL_SHUTDOWN; Label: Manual shutdown; Value: 6
bitfield32 | Evt1 |  |  | Name: OVER_TEMP; Label: Over temperature; Value: 7
bitfield32 | Evt1 |  |  | Name: OVER_FREQUENCY; Label: Frequency above limit; Value: 8
bitfield32 | Evt1 |  |  | Name: UNDER_FREQUENCY; Label: Frequency under limit; Value: 9
bitfield32 | Evt1 |  |  | Name: AC_OVER_VOLT; Label: AC Voltage above limit; Value: 10
bitfield32 | Evt1 |  |  | Name: AC_UNDER_VOLT; Label: AC Voltage under limit; Value: 11
bitfield32 | Evt1 |  |  | Name: BLOWN_STRING_FUSE; Label: Blown String fuse on input; Value: 12
bitfield32 | Evt1 |  |  | Name: UNDER_TEMP; Label: Under temperature; Value: 13
bitfield32 | Evt1 |  |  | Name: MEMORY_LOSS; Label: Generic Memory or Communication error (internal); Value: 14
bitfield32 | Evt1 |  |  | Name: HW_TEST_FAILURE; Label: Hardware test failure; Value: 15

## 111
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Inverter (Single Phase) FLOAT | 111 | uint16 |  |  | R | M | Include this model for single phase inverter monitoring using float values
Header |  | 1 |  | 1 | L |  | 60 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 2 | A | Amps |  | float32 | A |  | R | M | AC Current
Fixed Block |  | 4 | 2 | 2 | AphA | Amps PhaseA |  | float32 | A |  | R | M | Phase A Current | Connected Phase
Fixed Block |  | 6 | 4 | 2 | AphB | Amps PhaseB |  | float32 | A |  | R | O | Phase B Current
Fixed Block |  | 8 | 6 | 2 | AphC | Amps PhaseC |  | float32 | A |  | R | O | Phase C Current
Fixed Block |  | 10 | 8 | 2 | PPVphAB | Phase Voltage AB |  | float32 | V |  | R | O | Phase Voltage AB
Fixed Block |  | 12 | 10 | 2 | PPVphBC | Phase Voltage BC |  | float32 | V |  | R | O | Phase Voltage BC
Fixed Block |  | 14 | 12 | 2 | PPVphCA | Phase Voltage CA |  | float32 | V |  | R | O | Phase Voltage CA
Fixed Block |  | 16 | 14 | 2 | PhVphA | Phase Voltage AN |  | float32 | V |  | R | M | Phase Voltage AN
Fixed Block |  | 18 | 16 | 2 | PhVphB | Phase Voltage BN |  | float32 | V |  | R | O | Phase Voltage BN
Fixed Block |  | 20 | 18 | 2 | PhVphC | Phase Voltage CN |  | float32 | V |  | R | O | Phase Voltage CN
Fixed Block |  | 22 | 20 | 2 | W | Watts |  | float32 | W |  | R | M | AC Power
Fixed Block |  | 24 | 22 | 2 | Hz | Hz |  | float32 | Hz |  | R | M | Line Frequency
Fixed Block |  | 26 | 24 | 2 | VA | VA |  | float32 | VA |  | R | O | AC Apparent Power
Fixed Block |  | 28 | 26 | 2 | VAr | VAr |  | float32 | var |  | R | O | AC Reactive Power
Fixed Block |  | 30 | 28 | 2 | PF | PF |  | float32 | Pct |  | R | O | AC Power Factor
Fixed Block |  | 32 | 30 | 2 | WH | WattHours |  | float32 | Wh |  | R | M | AC Energy
Fixed Block |  | 34 | 32 | 2 | DCA | DC Amps |  | float32 | A |  | R | O | DC Current
Fixed Block |  | 36 | 34 | 2 | DCV | DC Voltage |  | float32 | V |  | R | O | DC Voltage
Fixed Block |  | 38 | 36 | 2 | DCW | DC Watts |  | float32 | W |  | R | O | DC Power
Fixed Block |  | 40 | 38 | 2 | TmpCab | Cabinet Temperature |  | float32 | C |  | R | M | Cabinet Temperature
Fixed Block |  | 42 | 40 | 2 | TmpSnk | Heat Sink Temperature |  | float32 | C |  | R | O | Heat Sink Temperature
Fixed Block |  | 44 | 42 | 2 | TmpTrns | Transformer Temperature |  | float32 | C |  | R | O | Transformer Temperature
Fixed Block |  | 46 | 44 | 2 | TmpOt | Other Temperature |  | float32 | C |  | R | O | Other Temperature
Fixed Block |  | 48 | 46 | 1 | St | Operating State |  | enum16 |  |  | R | M | Enumerated value. Operating state
Fixed Block |  | 49 | 47 | 1 | StVnd | Vendor Operating State |  | enum16 |  |  | R | O | Vendor specific operating state code
Fixed Block |  | 50 | 48 | 2 | Evt1 | Event1 |  | bitfield32 |  |  | R | M | Bitmask value. Event fields
Fixed Block |  | 52 | 50 | 2 | Evt2 | Event Bitfield 2 |  | bitfield32 |  |  | R | M | Reserved for future use
Fixed Block |  | 54 | 52 | 2 | EvtVnd1 | Vendor Event Bitfield 1 |  | bitfield32 |  |  | R | O | Vendor defined events
Fixed Block |  | 56 | 54 | 2 | EvtVnd2 | Vendor Event Bitfield 2 |  | bitfield32 |  |  | R | O | Vendor defined events
Fixed Block |  | 58 | 56 | 2 | EvtVnd3 | Vendor Event Bitfield 3 |  | bitfield32 |  |  | R | O | Vendor defined events
Fixed Block |  | 60 | 58 | 2 | EvtVnd4 | Vendor Event Bitfield 4 |  | bitfield32 |  |  | R | O | Vendor defined events
enum16 | St |  |  | Name: ggOFF; Value: 1
enum16 | St |  |  | Name: ggSLEEPING; Value: 2
enum16 | St |  |  | Name: ggSTARTING; Value: 3
enum16 | St |  |  | Name: ggMPPT; Label: MPPT; Value: 4 |  | Device is auto tracking maximum power point
enum16 | St |  |  | Name: ggTHROTTLED; Value: 5
enum16 | St |  |  | Name: ggSHUTTING_DOWN; Value: 6
enum16 | St |  |  | Name: ggFAULT; Value: 7
enum16 | St |  |  | Name: ggSTANDBY; Value: 8
enum16 | St |  |  | Label: Off; Value: 8 |  | Device is not operating
enum16 | St |  |  | Label: Sleeping; Value: 8 |  | Device is sleeping / auto-shudown
enum16 | St |  |  | Label: Starting; Value: 8 |  | Device is staring up
enum16 | St |  |  | Label: Throttled; Value: 8 |  | Device is operating at reduced power output
enum16 | St |  |  | Label: Shutting down; Value: 8 |  | Device is shutting down
enum16 | St |  |  | Label: Fault; Value: 8 |  | One or more faults exist
enum16 | St |  |  | Label: Standby; Value: 8 |  | Device is in standby mode
bitfield32 | Evt1 |  |  | Name: GROUND_FAULT; Label: Ground fault; Value: 0
bitfield32 | Evt1 |  |  | Name: DC_OVER_VOLT; Label: DC over voltage; Value: 1
bitfield32 | Evt1 |  |  | Name: AC_DISCONNECT; Label: AC disconnect open; Value: 2
bitfield32 | Evt1 |  |  | Name: DC_DISCONNECT; Label: DC disconnect open; Value: 3
bitfield32 | Evt1 |  |  | Name: GRID_DISCONNECT; Label: Grid shutdown; Value: 4
bitfield32 | Evt1 |  |  | Name: CABINET_OPEN; Label: Cabinet open; Value: 5
bitfield32 | Evt1 |  |  | Name: MANUAL_SHUTDOWN; Label: Manual shutdown; Value: 6
bitfield32 | Evt1 |  |  | Name: OVER_TEMP; Label: Over temperature; Value: 7
bitfield32 | Evt1 |  |  | Name: OVER_FREQUENCY; Label: Frequency above limit; Value: 8
bitfield32 | Evt1 |  |  | Name: UNDER_FREQUENCY; Label: Frequency under limit; Value: 9
bitfield32 | Evt1 |  |  | Name: AC_OVER_VOLT; Label: AC Voltage above limit; Value: 10
bitfield32 | Evt1 |  |  | Name: AC_UNDER_VOLT; Label: AC Voltage under limit; Value: 11
bitfield32 | Evt1 |  |  | Name: BLOWN_STRING_FUSE; Label: Blown String fuse on input; Value: 12
bitfield32 | Evt1 |  |  | Name: UNDER_TEMP; Label: Under temperature; Value: 13
bitfield32 | Evt1 |  |  | Name: MEMORY_LOSS; Label: Generic Memory or Communication error (internal); Value: 14
bitfield32 | Evt1 |  |  | Name: HW_TEST_FAILURE; Label: Hardware test failure; Value: 15

## 112
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Inverter (Split Phase) FLOAT | 112 | uint16 |  |  | R | M | Include this model for split phase inverter monitoring using float values
Header |  | 1 |  | 1 | L |  | 60 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 2 | A | Amps |  | float32 | A |  | R | M | AC Current
Fixed Block |  | 4 | 2 | 2 | AphA | Amps PhaseA |  | float32 | A |  | R | M | Phase A Current | Connected Phase
Fixed Block |  | 6 | 4 | 2 | AphB | Amps PhaseB |  | float32 | A |  | R | M | Phase B Current | Connected Phase
Fixed Block |  | 8 | 6 | 2 | AphC | Amps PhaseC |  | float32 | A |  | R | O | Phase C Current
Fixed Block |  | 10 | 8 | 2 | PPVphAB | Phase Voltage AB |  | float32 | V |  | R | O | Phase Voltage AB
Fixed Block |  | 12 | 10 | 2 | PPVphBC | Phase Voltage BC |  | float32 | V |  | R | O | Phase Voltage BC
Fixed Block |  | 14 | 12 | 2 | PPVphCA | Phase Voltage CA |  | float32 | V |  | R | O | Phase Voltage CA
Fixed Block |  | 16 | 14 | 2 | PhVphA | Phase Voltage AN |  | float32 | V |  | R | M | Phase Voltage AN
Fixed Block |  | 18 | 16 | 2 | PhVphB | Phase Voltage BN |  | float32 | V |  | R | M | Phase Voltage BN
Fixed Block |  | 20 | 18 | 2 | PhVphC | Phase Voltage CN |  | float32 | V |  | R | O | Phase Voltage CN
Fixed Block |  | 22 | 20 | 2 | W | Watts |  | float32 | W |  | R | M | AC Power
Fixed Block |  | 24 | 22 | 2 | Hz | Hz |  | float32 | Hz |  | R | M | Line Frequency
Fixed Block |  | 26 | 24 | 2 | VA | VA |  | float32 | VA |  | R | O | AC Apparent Power
Fixed Block |  | 28 | 26 | 2 | VAr | VAr |  | float32 | var |  | R | O | AC Reactive Power
Fixed Block |  | 30 | 28 | 2 | PF | PF |  | float32 | Pct |  | R | O | AC Power Factor
Fixed Block |  | 32 | 30 | 2 | WH | WattHours |  | float32 | Wh |  | R | M | AC Energy
Fixed Block |  | 34 | 32 | 2 | DCA | DC Amps |  | float32 | A |  | R | O | DC Current
Fixed Block |  | 36 | 34 | 2 | DCV | DC Voltage |  | float32 | V |  | R | O | DC Voltage
Fixed Block |  | 38 | 36 | 2 | DCW | DC Watts |  | float32 | W |  | R | O | DC Power
Fixed Block |  | 40 | 38 | 2 | TmpCab | Cabinet Temperature |  | float32 | C |  | R | M | Cabinet Temperature
Fixed Block |  | 42 | 40 | 2 | TmpSnk | Heat Sink Temperature |  | float32 | C |  | R | O | Heat Sink Temperature
Fixed Block |  | 44 | 42 | 2 | TmpTrns | Transformer Temperature |  | float32 | C |  | R | O | Transformer Temperature
Fixed Block |  | 46 | 44 | 2 | TmpOt | Other Temperature |  | float32 | C |  | R | O | Other Temperature
Fixed Block |  | 48 | 46 | 1 | St | Operating State |  | enum16 |  |  | R | M | Enumerated value. Operating state
Fixed Block |  | 49 | 47 | 1 | StVnd | Vendor Operating State |  | enum16 |  |  | R | O | Vendor specific operating state code
Fixed Block |  | 50 | 48 | 2 | Evt1 | Event1 |  | bitfield32 |  |  | R | M | Bitmask value. Event fields
Fixed Block |  | 52 | 50 | 2 | Evt2 | Event Bitfield 2 |  | bitfield32 |  |  | R | M | Reserved for future use
Fixed Block |  | 54 | 52 | 2 | EvtVnd1 | Vendor Event Bitfield 1 |  | bitfield32 |  |  | R | O | Vendor defined events
Fixed Block |  | 56 | 54 | 2 | EvtVnd2 | Vendor Event Bitfield 2 |  | bitfield32 |  |  | R | O | Vendor defined events
Fixed Block |  | 58 | 56 | 2 | EvtVnd3 | Vendor Event Bitfield 3 |  | bitfield32 |  |  | R | O | Vendor defined events
Fixed Block |  | 60 | 58 | 2 | EvtVnd4 | Vendor Event Bitfield 4 |  | bitfield32 |  |  | R | O | Vendor defined events
enum16 | St |  |  | Name: OFF; Label: Off; Value: 1 |  | Device is not operating
enum16 | St |  |  | Name: SLEEPING; Label: Sleeping; Value: 2 |  | Device is sleeping / auto-shudown
enum16 | St |  |  | Name: STARTING; Label: Starting; Value: 3 |  | Device is staring up
enum16 | St |  |  | Name: MPPT; Label: MPPT; Value: 4 |  | Device is auto tracking maximum power point
enum16 | St |  |  | Name: THROTTLED; Label: Throttled; Value: 5 |  | Device is operating at reduced power output
enum16 | St |  |  | Name: SHUTTING_DOWN; Label: Shutting down; Value: 6 |  | Device is shutting down
enum16 | St |  |  | Name: FAULT; Label: Fault; Value: 7 |  | One or more faults exist
enum16 | St |  |  | Name: STANDBY; Label: Standby; Value: 8 |  | Device is in standby mode
bitfield32 | Evt1 |  |  | Name: GROUND_FAULT; Label: Ground fault; Value: 0
bitfield32 | Evt1 |  |  | Name: DC_OVER_VOLT; Label: DC over voltage; Value: 1
bitfield32 | Evt1 |  |  | Name: AC_DISCONNECT; Label: AC disconnect open; Value: 2
bitfield32 | Evt1 |  |  | Name: DC_DISCONNECT; Label: DC disconnect open; Value: 3
bitfield32 | Evt1 |  |  | Name: GRID_DISCONNECT; Label: Grid shutdown; Value: 4
bitfield32 | Evt1 |  |  | Name: CABINET_OPEN; Label: Cabinet open; Value: 5
bitfield32 | Evt1 |  |  | Name: MANUAL_SHUTDOWN; Label: Manual shutdown; Value: 6
bitfield32 | Evt1 |  |  | Name: OVER_TEMP; Label: Over temperature; Value: 7
bitfield32 | Evt1 |  |  | Name: OVER_FREQUENCY; Label: Frequency above limit; Value: 8
bitfield32 | Evt1 |  |  | Name: UNDER_FREQUENCY; Label: Frequency under limit; Value: 9
bitfield32 | Evt1 |  |  | Name: AC_OVER_VOLT; Label: AC Voltage above limit; Value: 10
bitfield32 | Evt1 |  |  | Name: AC_UNDER_VOLT; Label: AC Voltage under limit; Value: 11
bitfield32 | Evt1 |  |  | Name: BLOWN_STRING_FUSE; Label: Blown String fuse on input; Value: 12
bitfield32 | Evt1 |  |  | Name: UNDER_TEMP; Label: Under temperature; Value: 13
bitfield32 | Evt1 |  |  | Name: MEMORY_LOSS; Label: Generic Memory or Communication error (internal); Value: 14
bitfield32 | Evt1 |  |  | Name: HW_TEST_FAILURE; Label: Hardware test failure; Value: 15

## 113
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Inverter (Three Phase) FLOAT | 113 | uint16 |  |  | R | M | Include this model for three phase inverter monitoring using float values
Header |  | 1 |  | 1 | L |  | 60 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 2 | A | Amps |  | float32 | A |  | R | M | AC Current | Sum of active phases
Fixed Block |  | 4 | 2 | 2 | AphA | Amps PhaseA |  | float32 | A |  | R | M | Phase A Current | Connected Phase
Fixed Block |  | 6 | 4 | 2 | AphB | Amps PhaseB |  | float32 | A |  | R | M | Phase B Current | Connected Phase
Fixed Block |  | 8 | 6 | 2 | AphC | Amps PhaseC |  | float32 | A |  | R | M | Phase C Current | Connected Phase
Fixed Block |  | 10 | 8 | 2 | PPVphAB | Phase Voltage AB |  | float32 | V |  | R | O | Phase Voltage AB
Fixed Block |  | 12 | 10 | 2 | PPVphBC | Phase Voltage BC |  | float32 | V |  | R | O | Phase Voltage BC
Fixed Block |  | 14 | 12 | 2 | PPVphCA | Phase Voltage CA |  | float32 | V |  | R | O | Phase Voltage CA
Fixed Block |  | 16 | 14 | 2 | PhVphA | Phase Voltage AN |  | float32 | V |  | R | M | Phase Voltage AN
Fixed Block |  | 18 | 16 | 2 | PhVphB | Phase Voltage BN |  | float32 | V |  | R | M | Phase Voltage BN
Fixed Block |  | 20 | 18 | 2 | PhVphC | Phase Voltage CN |  | float32 | V |  | R | M | Phase Voltage CN
Fixed Block |  | 22 | 20 | 2 | W | Watts |  | float32 | W |  | R | M | AC Power
Fixed Block |  | 24 | 22 | 2 | Hz | Hz |  | float32 | Hz |  | R | M | Line Frequency
Fixed Block |  | 26 | 24 | 2 | VA | VA |  | float32 | VA |  | R | O | AC Apparent Power
Fixed Block |  | 28 | 26 | 2 | VAr | VAr |  | float32 | var |  | R | O | AC Reactive Power
Fixed Block |  | 30 | 28 | 2 | PF | PF |  | float32 | Pct |  | R | O | AC Power Factor
Fixed Block |  | 32 | 30 | 2 | WH | WattHours |  | float32 | Wh |  | R | M | AC Energy
Fixed Block |  | 34 | 32 | 2 | DCA | DC Amps |  | float32 | A |  | R | O | DC Current
Fixed Block |  | 36 | 34 | 2 | DCV | DC Voltage |  | float32 | V |  | R | O | DC Voltage
Fixed Block |  | 38 | 36 | 2 | DCW | DC Watts |  | float32 | W |  | R | O | DC Power
Fixed Block |  | 40 | 38 | 2 | TmpCab | Cabinet Temperature |  | float32 | C |  | R | M | Cabinet Temperature
Fixed Block |  | 42 | 40 | 2 | TmpSnk | Heat Sink Temperature |  | float32 | C |  | R | O | Heat Sink Temperature
Fixed Block |  | 44 | 42 | 2 | TmpTrns | Transformer Temperature |  | float32 | C |  | R | O | Transformer Temperature
Fixed Block |  | 46 | 44 | 2 | TmpOt | Other Temperature |  | float32 | C |  | R | O | Other Temperature
Fixed Block |  | 48 | 46 | 1 | St | Operating State |  | enum16 |  |  | R | M | Enumerated value. Operating state
Fixed Block |  | 49 | 47 | 1 | StVnd | Vendor Operating State |  | enum16 |  |  | R | O | Vendor specific operating state code
Fixed Block |  | 50 | 48 | 2 | Evt1 | Event1 |  | bitfield32 |  |  | R | M | Bitmask value. Event fields
Fixed Block |  | 52 | 50 | 2 | Evt2 | Event Bitfield 2 |  | bitfield32 |  |  | R | M | Reserved for future use
Fixed Block |  | 54 | 52 | 2 | EvtVnd1 | Vendor Event Bitfield 1 |  | bitfield32 |  |  | R | O | Vendor defined events
Fixed Block |  | 56 | 54 | 2 | EvtVnd2 | Vendor Event Bitfield 2 |  | bitfield32 |  |  | R | O | Vendor defined events
Fixed Block |  | 58 | 56 | 2 | EvtVnd3 | Vendor Event Bitfield 3 |  | bitfield32 |  |  | R | O | Vendor defined events
Fixed Block |  | 60 | 58 | 2 | EvtVnd4 | Vendor Event Bitfield 4 |  | bitfield32 |  |  | R | O | Vendor defined events
enum16 | St |  |  | Name: OFF; Label: Off; Value: 1 |  | Device is not operating
enum16 | St |  |  | Name: SLEEPING; Label: Sleeping; Value: 2 |  | Device is sleeping / auto-shudown
enum16 | St |  |  | Name: STARTING; Label: Starting; Value: 3 |  | Device is staring up
enum16 | St |  |  | Name: MPPT; Label: MPPT; Value: 4 |  | Device is auto tracking maximum power point
enum16 | St |  |  | Name: THROTTLED; Label: Throttled; Value: 5 |  | Device is operating at reduced power output
enum16 | St |  |  | Name: SHUTTING_DOWN; Label: Shutting down; Value: 6 |  | Device is shutting down
enum16 | St |  |  | Name: FAULT; Label: Fault; Value: 7 |  | One or more faults exist
enum16 | St |  |  | Name: STANDBY; Label: Standby; Value: 8 |  | Device is in standby mode
bitfield32 | Evt1 |  |  | Name: GROUND_FAULT; Label: Ground fault; Value: 0
bitfield32 | Evt1 |  |  | Name: DC_OVER_VOLT; Label: DC over voltage; Value: 1
bitfield32 | Evt1 |  |  | Name: AC_DISCONNECT; Label: AC disconnect open; Value: 2
bitfield32 | Evt1 |  |  | Name: DC_DISCONNECT; Label: DC disconnect open; Value: 3
bitfield32 | Evt1 |  |  | Name: GRID_DISCONNECT; Label: Grid shutdown; Value: 4
bitfield32 | Evt1 |  |  | Name: CABINET_OPEN; Label: Cabinet open; Value: 5
bitfield32 | Evt1 |  |  | Name: MANUAL_SHUTDOWN; Label: Manual shutdown; Value: 6
bitfield32 | Evt1 |  |  | Name: OVER_TEMP; Label: Over temperature; Value: 7
bitfield32 | Evt1 |  |  | Name: OVER_FREQUENCY; Label: Frequency above limit; Value: 8
bitfield32 | Evt1 |  |  | Name: UNDER_FREQUENCY; Label: Frequency under limit; Value: 9
bitfield32 | Evt1 |  |  | Name: AC_OVER_VOLT; Label: AC Voltage above limit; Value: 10
bitfield32 | Evt1 |  |  | Name: AC_UNDER_VOLT; Label: AC Voltage under limit; Value: 11
bitfield32 | Evt1 |  |  | Name: BLOWN_STRING_FUSE; Label: Blown String fuse on input; Value: 12
bitfield32 | Evt1 |  |  | Name: UNDER_TEMP; Label: Under temperature; Value: 13
bitfield32 | Evt1 |  |  | Name: MEMORY_LOSS; Label: Generic Memory or Communication error (internal); Value: 14
bitfield32 | Evt1 |  |  | Name: HW_TEST_FAILURE; Label: Hardware test failure; Value: 15

## 120
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Nameplate | 120 | uint16 |  |  | R | M | Inverter Controls Nameplate Ratings | Ref 3: 8.14.3.2, Ref 4: 17
Header |  | 1 |  | 1 | L |  | 26 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | DERTyp | DERTyp |  | enum16 |  |  | R | M | Type of DER device. Default value is 4 to indicate PV device.
Fixed Block |  | 3 | 1 | 1 | WRtg | WRtg |  | uint16 | W | WRtg_SF | R | M | Continuous power output capability of the inverter.
Fixed Block |  | 4 | 2 | 1 | WRtg_SF | WRtg_SF |  | sunssf |  |  | R | M | Scale factor
Fixed Block |  | 5 | 3 | 1 | VARtg | VARtg |  | uint16 | VA | VARtg_SF | R | M | Continuous Volt-Ampere capability of the inverter.
Fixed Block |  | 6 | 4 | 1 | VARtg_SF | VARtg_SF |  | sunssf |  |  | R | M | Scale factor
Fixed Block |  | 7 | 5 | 1 | VArRtgQ1 | VArRtgQ1 |  | int16 | var | VArRtg_SF | R | M | Continuous VAR capability of the inverter in quadrant 1.
Fixed Block |  | 8 | 6 | 1 | VArRtgQ2 | VArRtgQ2 |  | int16 | var | VArRtg_SF | R | M | Continuous VAR capability of the inverter in quadrant 2.
Fixed Block |  | 9 | 7 | 1 | VArRtgQ3 | VArRtgQ3 |  | int16 | var | VArRtg_SF | R | M | Continuous VAR capability of the inverter in quadrant 3.
Fixed Block |  | 10 | 8 | 1 | VArRtgQ4 | VArRtgQ4 |  | int16 | var | VArRtg_SF | R | M | Continuous VAR capability of the inverter in quadrant 4.
Fixed Block |  | 11 | 9 | 1 | VArRtg_SF | VArRtg_SF |  | sunssf |  |  | R | M | Scale factor
Fixed Block |  | 12 | 10 | 1 | ARtg | ARtg |  | uint16 | A | ARtg_SF | R | M | Maximum RMS AC current level capability of the inverter. | Sum of all connected phases. Current rating under nominal voltage under nominal power factor.
Fixed Block |  | 13 | 11 | 1 | ARtg_SF | ARtg_SF |  | sunssf |  |  | R | M | Scale factor
Fixed Block |  | 14 | 12 | 1 | PFRtgQ1 | PFRtgQ1 |  | int16 | cos() | PFRtg_SF | R | M | Minimum power factor capability of the inverter in quadrant 1. | EEI sign convention.
Fixed Block |  | 15 | 13 | 1 | PFRtgQ2 | PFRtgQ2 |  | int16 | cos() | PFRtg_SF | R | M | Minimum power factor capability of the inverter in quadrant 2. | EEI sign convention.
Fixed Block |  | 16 | 14 | 1 | PFRtgQ3 | PFRtgQ3 |  | int16 | cos() | PFRtg_SF | R | M | Minimum power factor capability of the inverter in quadrant 3. | EEI sign convention.
Fixed Block |  | 17 | 15 | 1 | PFRtgQ4 | PFRtgQ4 |  | int16 | cos() | PFRtg_SF | R | M | Minimum power factor capability of the inverter in quadrant 4. | EEI sign convention.
Fixed Block |  | 18 | 16 | 1 | PFRtg_SF | PFRtg_SF |  | sunssf |  |  | R | M | Scale factor
Fixed Block |  | 19 | 17 | 1 | WHRtg | WHRtg |  | uint16 | Wh | WHRtg_SF | R | O | Nominal energy rating of storage device.
Fixed Block |  | 20 | 18 | 1 | WHRtg_SF | WHRtg_SF |  | sunssf |  |  | R | O | Scale factor
Fixed Block |  | 21 | 19 | 1 | AhrRtg | AhrRtg |  | uint16 | AH | AhrRtg_SF | R | O | The useable capacity of the battery. Maximum charge minus minimum charge from a technology capability perspective (Amp-hour capacity rating).
Fixed Block |  | 22 | 20 | 1 | AhrRtg_SF | AhrRtg_SF |  | sunssf |  |  | R | O | Scale factor for amp-hour rating.
Fixed Block |  | 23 | 21 | 1 | MaxChaRte | MaxChaRte |  | uint16 | W | MaxChaRte_SF | R | O | Maximum rate of energy transfer into the storage device.
Fixed Block |  | 24 | 22 | 1 | MaxChaRte_SF | MaxChaRte_SF |  | sunssf |  |  | R | O | Scale factor
Fixed Block |  | 25 | 23 | 1 | MaxDisChaRte | MaxDisChaRte |  | uint16 | W | MaxDisChaRte_SF | R | O | Maximum rate of energy transfer out of the storage device.
Fixed Block |  | 26 | 24 | 1 | MaxDisChaRte_SF | MaxDisChaRte_SF |  | sunssf |  |  | R | O | Scale factor
Fixed Block |  | 27 | 25 | 1 | Pad | Pad |  | pad |  |  | R | O | Pad register.
enum16 | DERTyp |  |  | Name: PV; Value: 4
enum16 | DERTyp |  |  | Name: PV_STOR; Value: 82

## 121
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Basic Settings | 121 | uint16 |  |  | R | M | Inverter Controls Basic Settings | Ref 3: 8.4.2.1, Ref 4: 17
Header |  | 1 |  | 1 | L |  | 30 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | WMax | WMax |  | uint16 | W | WMax_SF | RW | M | Setting for maximum power output. Default to WRtg.
Fixed Block |  | 3 | 1 | 1 | VRef | VRef |  | uint16 | V | VRef_SF | RW | M | Voltage at the PCC.
Fixed Block |  | 4 | 2 | 1 | VRefOfs | VRefOfs |  | int16 | V | VRefOfs_SF | RW | M | Offset from PCC to inverter.
Fixed Block |  | 5 | 3 | 1 | VMax | VMax |  | uint16 | V | VMinMax_SF | RW | O | Setpoint for maximum voltage.
Fixed Block |  | 6 | 4 | 1 | VMin | VMin |  | uint16 | V | VMinMax_SF | RW | O | Setpoint for minimum voltage.
Fixed Block |  | 7 | 5 | 1 | VAMax | VAMax |  | uint16 | VA | VAMax_SF | RW | O | Setpoint for maximum apparent power. Default to VARtg.
Fixed Block |  | 8 | 6 | 1 | VArMaxQ1 | VArMaxQ1 |  | int16 | var | VArMax_SF | RW | O | Setting for maximum reactive power in quadrant 1. Default to VArRtgQ1.
Fixed Block |  | 9 | 7 | 1 | VArMaxQ2 | VArMaxQ2 |  | int16 | var | VArMax_SF | RW | O | Setting for maximum reactive power in quadrant 2. Default to VArRtgQ2.
Fixed Block |  | 10 | 8 | 1 | VArMaxQ3 | VArMaxQ3 |  | int16 | var | VArMax_SF | RW | O | Setting for maximum reactive power in quadrant 3. Default to VArRtgQ3.
Fixed Block |  | 11 | 9 | 1 | VArMaxQ4 | VArMaxQ4 |  | int16 | var | VArMax_SF | RW | O | Setting for maximum reactive power in quadrant 4. Default to VArRtgQ4.
Fixed Block |  | 12 | 10 | 1 | WGra | WGra |  | uint16 | % WMax/sec | WGra_SF | RW | O | Default ramp rate of change of active power due to command or internal action.
Fixed Block |  | 13 | 11 | 1 | PFMinQ1 | PFMinQ1 |  | int16 | cos() | PFMin_SF | RW | O | Setpoint for minimum power factor value in quadrant 1. Default to PFRtgQ1. | EEI sign convention.
Fixed Block |  | 14 | 12 | 1 | PFMinQ2 | PFMinQ2 |  | int16 | cos() | PFMin_SF | RW | O | Setpoint for minimum power factor value in quadrant 2. Default to PFRtgQ2. | EEI sign convention.
Fixed Block |  | 15 | 13 | 1 | PFMinQ3 | PFMinQ3 |  | int16 | cos() | PFMin_SF | RW | O | Setpoint for minimum power factor value in quadrant 3. Default to PFRtgQ3. | EEI sign convention.
Fixed Block |  | 16 | 14 | 1 | PFMinQ4 | PFMinQ4 |  | int16 | cos() | PFMin_SF | RW | O | Setpoint for minimum power factor value in quadrant 4. Default to PFRtgQ4. | EEI sign convention.
Fixed Block |  | 17 | 15 | 1 | VArAct | VArAct |  | enum16 |  |  | RW | O | VAR action on change between charging and discharging: 1=switch 2=maintain VAR characterization.
Fixed Block |  | 18 | 16 | 1 | ClcTotVA | ClcTotVA |  | enum16 |  |  | RW | O | Calculation method for total apparent power. 1=vector 2=arithmetic.
Fixed Block |  | 19 | 17 | 1 | MaxRmpRte | MaxRmpRte |  | uint16 | % WGra | MaxRmpRte_SF | RW | O | Setpoint for maximum ramp rate as percentage of nominal maximum ramp rate. This setting will limit the rate that watts delivery to the grid can increase or decrease in response to intermittent PV generation.
Fixed Block |  | 20 | 18 | 1 | ECPNomHz | ECPNomHz |  | uint16 | Hz | ECPNomHz_SF | RW | O | Setpoint for nominal frequency at the ECP.
Fixed Block |  | 21 | 19 | 1 | ConnPh | ConnPh |  | enum16 |  |  | RW | O | Identity of connected phase for single phase inverters. A=1 B=2 C=3.
Fixed Block |  | 22 | 20 | 1 | WMax_SF | WMax_SF |  | sunssf |  |  | R | M | Scale factor for real power.
Fixed Block |  | 23 | 21 | 1 | VRef_SF | VRef_SF |  | sunssf |  |  | R | M | Scale factor for voltage at the PCC.
Fixed Block |  | 24 | 22 | 1 | VRefOfs_SF | VRefOfs_SF |  | sunssf |  |  | R | M | Scale factor for offset voltage.
Fixed Block |  | 25 | 23 | 1 | VMinMax_SF | VMinMax_SF |  | sunssf |  |  | R | O | Scale factor for min/max voltages.
Fixed Block |  | 26 | 24 | 1 | VAMax_SF | VAMax_SF |  | sunssf |  |  | R | O | Scale factor for apparent power.
Fixed Block |  | 27 | 25 | 1 | VArMax_SF | VArMax_SF |  | sunssf |  |  | R | O | Scale factor for reactive power.
Fixed Block |  | 28 | 26 | 1 | WGra_SF | WGra_SF |  | sunssf |  |  | R | O | Scale factor for default ramp rate.
Fixed Block |  | 29 | 27 | 1 | PFMin_SF | PFMin_SF |  | sunssf |  |  | R | O | Scale factor for minimum power factor.
Fixed Block |  | 30 | 28 | 1 | MaxRmpRte_SF | MaxRmpRte_SF |  | sunssf |  |  | R | O | Scale factor for maximum ramp percentage.
Fixed Block |  | 31 | 29 | 1 | ECPNomHz_SF | ECPNomHz_SF |  | sunssf |  |  | R | O | Scale factor for nominal frequency.
enum16 | VArAct |  |  | Name: SWITCH; Value: 1
enum16 | VArAct |  |  | Name: MAINTAIN; Value: 2
enum16 | ClcTotVA |  |  | Name: VECTOR; Value: 1
enum16 | ClcTotVA |  |  | Name: ARITHMETIC; Value: 2
enum16 | ConnPh | bar: Name; Value
enum16 | ConnPh |  |  | Name: B; Value: 2
enum16 | ConnPh |  |  | Name: C; Value: 3

## 122
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Measurements_Status | 122 | uint16 |  |  | R | M | Inverter Controls Extended Measurements and Status | Ref 3: 8.14.3.2, Ref 4: 17
Header |  | 1 |  | 1 | L |  | 44 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | PVConn | PVConn |  | bitfield16 |  |  | R | M | PV inverter present/available status. Enumerated value.
Fixed Block |  | 3 | 1 | 1 | StorConn | StorConn |  | bitfield16 |  |  | R | M | Storage inverter present/available status. Enumerated value.
Fixed Block |  | 4 | 2 | 1 | ECPConn | ECPConn |  | bitfield16 |  |  | R | M | ECP connection status: disconnected=0 connected=1.
Fixed Block |  | 5 | 3 | 4 | ActWh | ActWh |  | acc64 | Wh |  | R | O | AC lifetime active (real) energy output.
Fixed Block |  | 9 | 7 | 4 | ActVAh | ActVAh |  | acc64 | VAh |  | R | O | AC lifetime apparent energy output.
Fixed Block |  | 13 | 11 | 4 | ActVArhQ1 | ActVArhQ1 |  | acc64 | varh |  | R | O | AC lifetime reactive energy output in quadrant 1.
Fixed Block |  | 17 | 15 | 4 | ActVArhQ2 | ActVArhQ2 |  | acc64 | varh |  | R | O | AC lifetime reactive energy output in quadrant 2.
Fixed Block |  | 21 | 19 | 4 | ActVArhQ3 | ActVArhQ3 |  | acc64 | varh |  | R | O | AC lifetime negative energy output in quadrant 3.
Fixed Block |  | 25 | 23 | 4 | ActVArhQ4 | ActVArhQ4 |  | acc64 | varh |  | R | O | AC lifetime reactive energy output in quadrant 4.
Fixed Block |  | 29 | 27 | 1 | VArAval | VArAval |  | int16 | var | VArAval_SF | R | O | Amount of VARs available without impacting watts output.
Fixed Block |  | 30 | 28 | 1 | VArAval_SF | VArAval_SF |  | sunssf |  |  | R | O | Scale factor for available VARs.
Fixed Block |  | 31 | 29 | 1 | WAval | WAval |  | uint16 | var | WAval_SF | R | O | Amount of Watts available.
Fixed Block |  | 32 | 30 | 1 | WAval_SF | WAval_SF |  | sunssf |  |  | R | O | Scale factor for available Watts.
Fixed Block |  | 33 | 31 | 2 | StSetLimMsk | StSetLimMsk |  | bitfield32 |  |  | R | O | Bit Mask indicating setpoint limit(s) reached. | Bits shall be automatically cleared on read.
Fixed Block |  | 35 | 33 | 2 | StActCtl | StActCtl |  | bitfield32 |  |  | R | O | Bit Mask indicating which inverter controls are currently active.
Fixed Block |  | 37 | 35 | 4 | TmSrc | TmSrc |  | string |  |  | R | O | Source of time synchronization.
Fixed Block |  | 41 | 39 | 2 | Tms | Tms |  | uint32 | Secs |  | R | O | Seconds since 01-01-2000 00:00 UTC
Fixed Block |  | 43 | 41 | 1 | RtSt | RtSt |  | bitfield16 |  |  | R | O | Bit Mask indicating active ride-through status.
Fixed Block |  | 44 | 42 | 1 | Ris | Ris |  | uint16 | ohms | Ris_SF | R | O | Isolation resistance.
Fixed Block |  | 45 | 43 | 1 | Ris_SF | Ris_SF |  | sunssf |  |  | R | O | Scale factor for isolation resistance.
bitfield16 | PVConn |  |  | Name: CONNECTED; Value: 0
bitfield16 | PVConn |  |  | Name: AVAILABLE; Value: 1
bitfield16 | PVConn |  |  | Name: OPERATING; Value: 2
bitfield16 | PVConn |  |  | Name: TEST; Value: 3
bitfield16 | StorConn |  |  | Name: CONNECTED; Value: 0
bitfield16 | StorConn |  |  | Name: AVAILABLE; Value: 1
bitfield16 | StorConn |  |  | Name: OPERATING; Value: 2
bitfield16 | StorConn |  |  | Name: TEST; Value: 3
bitfield16 | ECPConn |  |  | Name: CONNECTED; Value: 0
bitfield32 | StSetLimMsk |  |  | Name: WMax; Value: 0
bitfield32 | StSetLimMsk |  |  | Name: VAMax; Value: 1
bitfield32 | StSetLimMsk |  |  | Name: VArAval; Value: 2
bitfield32 | StSetLimMsk |  |  | Name: VArMaxQ1; Value: 3
bitfield32 | StSetLimMsk |  |  | Name: VArMaxQ2; Value: 4
bitfield32 | StSetLimMsk |  |  | Name: VArMaxQ3; Value: 5
bitfield32 | StSetLimMsk |  |  | Name: VArMaxQ4; Value: 6
bitfield32 | StSetLimMsk |  |  | Name: PFMinQ1; Value: 7
bitfield32 | StSetLimMsk |  |  | Name: PFMinQ2; Value: 8
bitfield32 | StSetLimMsk |  |  | Name: PFMinQ3; Value: 9
bitfield32 | StSetLimMsk |  |  | Name: PFMinQ4; Value: 10
bitfield32 | StActCtl |  |  | Name: FixedW; Value: 0
bitfield32 | StActCtl |  |  | Name: FixedVAR; Value: 1
bitfield32 | StActCtl |  |  | Name: FixedPF; Value: 2
bitfield32 | StActCtl |  |  | Name: Volt-VAr; Value: 3
bitfield32 | StActCtl |  |  | Name: Freq-Watt-Param; Value: 4
bitfield32 | StActCtl |  |  | Name: Freq-Watt-Curve; Value: 5
bitfield32 | StActCtl |  |  | Name: Dyn-Reactive-Current; Value: 6
bitfield32 | StActCtl |  |  | Name: LVRT; Value: 7
bitfield32 | StActCtl |  |  | Name: HVRT; Value: 8
bitfield32 | StActCtl |  |  | Name: Watt-PF; Value: 9
bitfield32 | StActCtl |  |  | Name: Volt-Watt; Value: 10
bitfield32 | StActCtl |  |  | Name: Scheduled; Value: 12
bitfield32 | StActCtl |  |  | Name: LFRT; Value: 13
bitfield32 | StActCtl |  |  | Name: HFRT; Value: 14
bitfield16 | RtSt |  |  | Name: LVRT_ACTIVE; Value: 0
bitfield16 | RtSt |  |  | Name: HVRT_ACTIVE; Value: 1
bitfield16 | RtSt |  |  | Name: LFRT_ACTIVE; Value: 2
bitfield16 | RtSt |  |  | Name: HFRT_ACTIVE; Value: 3

## 123
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Immediate Controls | 123 | uint16 |  |  | R | M | Immediate Inverter Controls | Ref 3: 8.7.1.2, 8.7.2.2, 8.7.3.2
Header |  | 1 |  | 1 | L |  | 24 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | Conn_WinTms | Conn_WinTms |  | uint16 | Secs |  | RW | O | Time window for connect/disconnect.
Fixed Block |  | 3 | 1 | 1 | Conn_RvrtTms | Conn_RvrtTms |  | uint16 | Secs |  | RW | O | Timeout period for connect/disconnect.
Fixed Block |  | 4 | 2 | 1 | Conn | Conn |  | enum16 |  |  | RW | M | Enumerated valued. Connection control.
Fixed Block |  | 5 | 3 | 1 | WMaxLimPct | WMaxLimPct |  | uint16 | % WMax | WMaxLimPct_SF | RW | M | Set power output to specified level.
Fixed Block |  | 6 | 4 | 1 | WMaxLimPct_WinTms | WMaxLimPct_WinTms |  | uint16 | Secs |  | RW | O | Time window for power limit change.
Fixed Block |  | 7 | 5 | 1 | WMaxLimPct_RvrtTms | WMaxLimPct_RvrtTms |  | uint16 | Secs |  | RW | O | Timeout period for power limit.
Fixed Block |  | 8 | 6 | 1 | WMaxLimPct_RmpTms | WMaxLimPct_RmpTms |  | uint16 | Secs |  | RW | O | Ramp time for moving from current setpoint to new setpoint.
Fixed Block |  | 9 | 7 | 1 | WMaxLim_Ena | WMaxLim_Ena |  | enum16 |  |  | RW | M | Enumerated valued. Throttle enable/disable control.
Fixed Block |  | 10 | 8 | 1 | OutPFSet | OutPFSet |  | int16 | cos() | OutPFSet_SF | RW | M | Set power factor to specific value - cosine of angle.
Fixed Block |  | 11 | 9 | 1 | OutPFSet_WinTms | OutPFSet_WinTms |  | uint16 | Secs |  | RW | O | Time window for power factor change.
Fixed Block |  | 12 | 10 | 1 | OutPFSet_RvrtTms | OutPFSet_RvrtTms |  | uint16 | Secs |  | RW | O | Timeout period for power factor.
Fixed Block |  | 13 | 11 | 1 | OutPFSet_RmpTms | OutPFSet_RmpTms |  | uint16 | Secs |  | RW | O | Ramp time for moving from current setpoint to new setpoint.
Fixed Block |  | 14 | 12 | 1 | OutPFSet_Ena | OutPFSet_Ena |  | enum16 |  |  | RW | M | Enumerated valued. Fixed power factor enable/disable control.
Fixed Block |  | 15 | 13 | 1 | VArWMaxPct | VArWMaxPct |  | int16 | % WMax | VArPct_SF | RW | O | Reactive power in percent of WMax.
Fixed Block |  | 16 | 14 | 1 | VArMaxPct | VArMaxPct |  | int16 | % VArMax | VArPct_SF | RW | O | Reactive power in percent of VArMax.
Fixed Block |  | 17 | 15 | 1 | VArAvalPct | VArAvalPct |  | int16 | % VArAval | VArPct_SF | RW | O | Reactive power in percent of VArAval.
Fixed Block |  | 18 | 16 | 1 | VArPct_WinTms | VArPct_WinTms |  | uint16 | Secs |  | RW | O | Time window for VAR limit change.
Fixed Block |  | 19 | 17 | 1 | VArPct_RvrtTms | VArPct_RvrtTms |  | uint16 | Secs |  | RW | O | Timeout period for VAR limit.
Fixed Block |  | 20 | 18 | 1 | VArPct_RmpTms | VArPct_RmpTms |  | uint16 | Secs |  | RW | O | Ramp time for moving from current setpoint to new setpoint.
Fixed Block |  | 21 | 19 | 1 | VArPct_Mod | VArPct_Mod |  | enum16 |  |  | RW | O | Enumerated value. VAR percent limit mode.
Fixed Block |  | 22 | 20 | 1 | VArPct_Ena | VArPct_Ena |  | enum16 |  |  | RW | M | Enumerated valued. Percent limit VAr enable/disable control.
Fixed Block |  | 23 | 21 | 1 | WMaxLimPct_SF | WMaxLimPct_SF |  | sunssf |  |  | R | M | Scale factor for power output percent.
Fixed Block |  | 24 | 22 | 1 | OutPFSet_SF | OutPFSet_SF |  | sunssf |  |  | R | M | Scale factor for power factor.
Fixed Block |  | 25 | 23 | 1 | VArPct_SF | VArPct_SF |  | sunssf |  |  | R | O | Scale factor for reactive power percent.
enum16 | Conn |  |  | Name: DISCONNECT; Value: 0
enum16 | Conn |  |  | Name: CONNECT; Value: 1
enum16 | WMaxLim_Ena |  |  | Name: DISABLED; Value: 0
enum16 | WMaxLim_Ena |  |  | Name: ENABLED; Value: 1
enum16 | OutPFSet_Ena |  |  | Name: DISABLED; Value: 0
enum16 | OutPFSet_Ena |  |  | Name: ENABLED; Value: 1
enum16 | VArPct_Mod |  |  | Name: NONE; Value: 0 |  | No VAR limit
enum16 | VArPct_Mod |  |  | Name: WMax; Value: 1 |  | VAR limit as a % of Wmax
enum16 | VArPct_Mod |  |  | Name: VArMax; Value: 2 |  | VAR limit as a % of VArMax
enum16 | VArPct_Mod |  |  | Name: VArAval; Value: 3 |  | VAR limit as a % of VArAval
enum16 | VArPct_Ena |  |  | Name: DISABLED; Value: 0
enum16 | VArPct_Ena |  |  | Name: ENABLED; Value: 1

## 124
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Storage | 124 | uint16 |  |  | R | M | Basic Storage Controls | Ref 3: 8.7.4.2
Header |  | 1 |  | 1 | L |  | 24 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | WChaMax | WChaMax |  | uint16 | W | WChaMax_SF | RW | M | Setpoint for maximum charge.
Fixed Block |  | 3 | 1 | 1 | WChaGra | WChaGra |  | uint16 | % WChaMax/sec | WChaDisChaGra_SF | RW | M | Setpoint for maximum charging rate. Default is MaxChaRte.
Fixed Block |  | 4 | 2 | 1 | WDisChaGra | WDisChaGra |  | uint16 | % WChaMax/sec | WChaDisChaGra_SF | RW | M | Setpoint for maximum discharge rate. Default is MaxDisChaRte.
Fixed Block |  | 5 | 3 | 1 | StorCtl_Mod | StorCtl_Mod |  | bitfield16 |  |  | RW | M | Activate hold/discharge/charge storage control mode. Bitfield value.
Fixed Block |  | 6 | 4 | 1 | VAChaMax | VAChaMax |  | uint16 | VA | VAChaMax_SF | RW | O | Setpoint for maximum charging VA.
Fixed Block |  | 7 | 5 | 1 | MinRsvPct | MinRsvPct |  | uint16 | % WChaMax | MinRsvPct_SF | RW | O | Setpoint for minimum reserve for storage as a percentage of the nominal maximum storage.
Fixed Block |  | 8 | 6 | 1 | ChaState | ChaState |  | uint16 | % AhrRtg | ChaState_SF | R | O | Currently available energy as a percent of the capacity rating.
Fixed Block |  | 9 | 7 | 1 | StorAval | StorAval |  | uint16 | AH | StorAval_SF | R | O | State of charge (ChaState) minus storage reserve (MinRsvPct) times capacity rating (AhrRtg).
Fixed Block |  | 10 | 8 | 1 | InBatV | InBatV |  | uint16 | V | InBatV_SF | R | O | Internal battery voltage.
Fixed Block |  | 11 | 9 | 1 | ChaSt | ChaSt |  | enum16 |  |  | R | O | Charge status of storage device. Enumerated value.
Fixed Block |  | 12 | 10 | 1 | OutWRte | OutWRte |  | int16 | % WDisChaMax | InOutWRte_SF | RW | O | Percent of max discharge rate.
Fixed Block |  | 13 | 11 | 1 | InWRte | InWRte |  | int16 | % WChaMax | InOutWRte_SF | RW | O | Percent of max charging rate.
Fixed Block |  | 14 | 12 | 1 | InOutWRte_WinTms | InOutWRte_WinTms |  | uint16 | Secs |  | RW | O | Time window for charge/discharge rate change.
Fixed Block |  | 15 | 13 | 1 | InOutWRte_RvrtTms | InOutWRte_RvrtTms |  | uint16 | Secs |  | RW | O | Timeout period for charge/discharge rate.
Fixed Block |  | 16 | 14 | 1 | InOutWRte_RmpTms | InOutWRte_RmpTms |  | uint16 | Secs |  | RW | O | Ramp time for moving from current setpoint to new setpoint.
Fixed Block |  | 17 | 15 | Size: 1; Name: ChaGriSet; Type: enum16; R/W: RW | O
Fixed Block |  | 18 | 16 | 1 | WChaMax_SF | WChaMax_SF |  | sunssf |  |  | R | M | Scale factor for maximum charge.
Fixed Block |  | 19 | 17 | 1 | WChaDisChaGra_SF | WChaDisChaGra_SF |  | sunssf |  |  | R | M | Scale factor for maximum charge and discharge rate.
Fixed Block |  | 20 | 18 | 1 | VAChaMax_SF | VAChaMax_SF |  | sunssf |  |  | R | O | Scale factor for maximum charging VA.
Fixed Block |  | 21 | 19 | 1 | MinRsvPct_SF | MinRsvPct_SF |  | sunssf |  |  | R | O | Scale factor for minimum reserve percentage.
Fixed Block |  | 22 | 20 | 1 | ChaState_SF | ChaState_SF |  | sunssf |  |  | R | O | Scale factor for available energy percent.
Fixed Block |  | 23 | 21 | 1 | StorAval_SF | StorAval_SF |  | sunssf |  |  | R | O | Scale factor for state of charge.
Fixed Block |  | 24 | 22 | 1 | InBatV_SF | InBatV_SF |  | sunssf |  |  | R | O | Scale factor for battery voltage.
Fixed Block |  | 25 | 23 | 1 | InOutWRte_SF | InOutWRte_SF |  | sunssf |  |  | R | O | Scale factor for percent charge/discharge rate.
bitfield16 | StorCtl_Mod |  |  | Name: CHARGE; Value: 0
bitfield16 | StorCtl_Mod |  |  | Name: DiSCHARGE; Value: 1
enum16 | ChaSt |  |  | Name: OFF; Value: 1
enum16 | ChaSt |  |  | Name: EMPTY; Value: 2
enum16 | ChaSt |  |  | Name: DISCHARGING; Value: 3
enum16 | ChaSt |  |  | Name: CHARGING; Value: 4
enum16 | ChaSt |  |  | Name: FULL; Value: 5
enum16 | ChaSt |  |  | Name: HOLDING; Value: 6
enum16 | ChaSt |  |  | Name: TESTING; Value: 7
enum16 | ChaGriSet |  |  | Name: PV; Value: 0
enum16 | ChaGriSet |  |  | Name: GRID; Value: 1

## 125
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Pricing | 125 | uint16 |  |  | R | M | Pricing Signal | Ref 3: 8.7.5.1; Ref 4: 6
Header |  | 1 |  | 1 | L |  | 8 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | ModEna | ModEna |  | bitfield16 |  |  | RW | M | Is price-based charge/dischage mode active?
Fixed Block |  | 3 | 1 | 1 | SigType | SigType |  | enum16 |  |  | RW | O | Meaning of the pricing signal. When a Price schedule is used, type must match the schedule range variable description.
Fixed Block |  | 4 | 2 | 1 | Sig | Sig |  | int16 |  | Sig_SF | RW | M | Utility/ESP specific pricing signal. Content depends on pricing signal type. When H/M/L type is specified. Low=0; Med=1; High=2.
Fixed Block |  | 5 | 3 | 1 | WinTms | WinTms |  | uint16 | Secs |  | RW | O | Time window for charge/discharge pricing change.
Fixed Block |  | 6 | 4 | 1 | RvtTms | RvtTms |  | uint16 | Secs |  | RW | O | Timeout period for charge/discharge pricing change.
Fixed Block |  | 7 | 5 | 1 | RmpTms | RmpTms |  | uint16 | Secs |  | RW | O | Ramp time for moving from current charge or discharge level to new level.
Fixed Block |  | 8 | 6 | 1 | Sig_SF | Sig_SF |  | sunssf |  |  | R | M | Pricing signal scale factor.
Fixed Block |  | 9 | 7 | Size: 1; Name: Pad; Type: pad; R/W: R | O
bitfield16 | ModEna |  |  | Name: ENABLE; Value: 0
enum16 | SigType |  |  | Name: UNKNOWN; Value: 0 |  | Signal type is unknown or other type of value
enum16 | SigType |  |  | Name: ABSOLUTE; Value: 1 |  | Signal is an absolute price value in local rate. E.g. 23 (cents/kWh)
enum16 | SigType |  |  | Name: RELATIVE; Value: 2 |  | Signal is a relative price in local rate. E.g. -5 (cents/kWh)
enum16 | SigType |  |  | Name: MULTIPLIER; Value: 3 |  | Signal is a price multiplier (percentage). E.g. 15 % uplift in the rate
enum16 | SigType |  |  | Name: LEVEL; Value: 4 |  | Signal is a price level. E.g. 0=lowest 1=low 2=normal 3=high 4=highest

## 126
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Static Volt-VAR | 126 | uint16 |  |  | R | M | Static Volt-VAR Arrays | Ref 3: 8.8.1.2
Header |  | 1 |  | 1 | L |  | 10 + (RB Count * 54) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | ActCrv | ActCrv |  | uint16 |  |  | RW | M | Index of active curve. 0=no active curve.
Fixed Block |  | 3 | 1 | 1 | ModEna | ModEna |  | bitfield16 |  |  | RW | M | Is Volt-VAR control active.
Fixed Block |  | 4 | 2 | 1 | WinTms | WinTms |  | uint16 | Secs |  | RW | O | Time window for volt-VAR change.
Fixed Block |  | 5 | 3 | 1 | RvrtTms | RvrtTms |  | uint16 | Secs |  | RW | O | Timeout period for volt-VAR curve selection.
Fixed Block |  | 6 | 4 | 1 | RmpTms | RmpTms |  | uint16 | Secs |  | RW | O | The time of the PT1 in seconds (time to accomplish a change of 95%).
Fixed Block |  | 7 | 5 | 1 | NCrv | NCrv |  | uint16 |  |  | R | M | Number of curves supported (recommend 4).
Fixed Block |  | 8 | 6 | 1 | NPt | NPt |  | uint16 |  |  | R | M | Number of curve points supported (maximum of 20).
Fixed Block |  | 9 | 7 | 1 | V_SF | V_SF |  | sunssf |  |  | R | M | Scale factor for percent VRef.
Fixed Block |  | 10 | 8 | 1 | DeptRef_SF | DeptRef_SF |  | sunssf |  |  | R | M | scale factor for dependent variable.
Fixed Block |  | 11 | 9 | 1 | RmpIncDec_SF | RmpIncDec_SF |  | sunssf |  |  | R | O | Scale factor for increment and decrement ramps.
Repeating Block |  | 12 | 0 | 1 | ActPt | ActPt |  | uint16 |  |  | RW | M | Number of active points in array.
Repeating Block |  | 13 | 1 | 1 | DeptRef | DeptRef |  | enum16 |  |  | RW | M | Meaning of dependent variable: 1=%WMax 2=%VArMax 3=%VArAval.
Repeating Block |  | 14 | 2 | 1 | V1 | V1 |  | uint16 | % VRef | V_SF | RW | M | Point 1 Volts.
Repeating Block |  | 15 | 3 | 1 | VAr1 | VAr1 |  | int16 |  | DeptRef_SF | RW | M | Point 1 VARs.
Repeating Block |  | 16 | 4 | 1 | V2 | V2 |  | uint16 | % VRef | V_SF | RW | O | Point 2 Volts.
Repeating Block |  | 17 | 5 | 1 | VAr2 | VAr2 |  | int16 |  | DeptRef_SF | RW | O | Point 2 VARs.
Repeating Block |  | 18 | 6 | 1 | V3 | V3 |  | uint16 | % VRef | V_SF | RW | O | Point 2 Volts.
Repeating Block |  | 19 | 7 | 1 | VAr3 | VAr3 |  | int16 | Various | DeptRef_SF | RW | O | Point 3 VARs.
Repeating Block |  | 20 | 8 | 1 | V4 | V4 |  | uint16 |  | V_SF | RW | O | Point 4 Volts.
Repeating Block |  | 21 | 9 | 1 | VAr4 | VAr4 |  | int16 |  | DeptRef_SF | RW | O | Point 4 VARs.
Repeating Block |  | 22 | 10 | 1 | V5 | V5 |  | uint16 | % VRef | V_SF | RW | O | Point 5 Volts.
Repeating Block |  | 23 | 11 | 1 | VAr5 | VAr5 |  | int16 |  | DeptRef_SF | RW | O | Point 5 VARs.
Repeating Block |  | 24 | 12 | 1 | V6 | V6 |  | uint16 | % VRef | V_SF | RW | O | Point 6 Volts.
Repeating Block |  | 25 | 13 | 1 | VAr6 | VAr6 |  | int16 |  | DeptRef_SF | RW | O | Point 6 VARs.
Repeating Block |  | 26 | 14 | 1 | V7 | V7 |  | uint16 | % VRef | V_SF | RW | O | Point 7 Volts.
Repeating Block |  | 27 | 15 | 1 | VAr7 | VAr7 |  | int16 |  | DeptRef_SF | RW | O | Point 7 VARs.
Repeating Block |  | 28 | 16 | 1 | V8 | V8 |  | uint16 | % VRef | V_SF | RW | O | Point 8 Volts.
Repeating Block |  | 29 | 17 | 1 | VAr8 | VAr8 |  | int16 |  | DeptRef_SF | RW | O | Point 8 VARs.
Repeating Block |  | 30 | 18 | 1 | V9 | V9 |  | uint16 | % VRef | V_SF | RW | O | Point 9 Volts.
Repeating Block |  | 31 | 19 | 1 | VAr9 | VAr9 |  | int16 |  | DeptRef_SF | RW | O | Point 9 VARs.
Repeating Block |  | 32 | 20 | 1 | V10 | V10 |  | uint16 | % VRef | V_SF | RW | O | Point 10 Volts.
Repeating Block |  | 33 | 21 | 1 | VAr10 | VAr10 |  | int16 |  | DeptRef_SF | RW | O | Point 10 VARs.
Repeating Block |  | 34 | 22 | 1 | V11 | V11 |  | uint16 | % VRef | V_SF | RW | O | Point 11 Volts.
Repeating Block |  | 35 | 23 | 1 | VAr11 | VAr11 |  | int16 |  | DeptRef_SF | RW | O | Point 11 VARs.
Repeating Block |  | 36 | 24 | 1 | V12 | V12 |  | uint16 | % VRef | V_SF | RW | O | Point 12 Volts.
Repeating Block |  | 37 | 25 | 1 | VAr12 | VAr12 |  | int16 |  | DeptRef_SF | RW | O | Point 12 VARs.
Repeating Block |  | 38 | 26 | 1 | V13 | V13 |  | uint16 | % VRef | V_SF | RW | O | Point 13 Volts.
Repeating Block |  | 39 | 27 | 1 | VAr13 | VAr13 |  | int16 |  | DeptRef_SF | RW | O | Point 13 VARs.
Repeating Block |  | 40 | 28 | 1 | V14 | V14 |  | uint16 | % VRef | V_SF | RW | O | Point 14 Volts.
Repeating Block |  | 41 | 29 | 1 | VAr14 | VAr14 |  | int16 |  | DeptRef_SF | RW | O | Point 14 VARs.
Repeating Block |  | 42 | 30 | 1 | V15 | V15 |  | uint16 | % VRef | V_SF | RW | O | Point 15 Volts.
Repeating Block |  | 43 | 31 | 1 | VAr15 | VAr15 |  | int16 |  | DeptRef_SF | RW | O | Point 15 VARs.
Repeating Block |  | 44 | 32 | 1 | V16 | V16 |  | uint16 | % VRef | V_SF | RW | O | Point 16 Volts.
Repeating Block |  | 45 | 33 | 1 | VAr16 | VAr16 |  | int16 |  | DeptRef_SF | RW | O | Point 16 VARs.
Repeating Block |  | 46 | 34 | 1 | V17 | V17 |  | uint16 | % VRef | V_SF | RW | O | Point 17 Volts.
Repeating Block |  | 47 | 35 | 1 | VAr17 | VAr17 |  | int16 |  | DeptRef_SF | RW | O | Point 17 VARs.
Repeating Block |  | 48 | 36 | 1 | V18 | V18 |  | uint16 | % VRef | V_SF | RW | O | Point 18 Volts.
Repeating Block |  | 49 | 37 | 1 | VAr18 | VAr18 |  | int16 |  | DeptRef_SF | RW | O | Point 18 VARs.
Repeating Block |  | 50 | 38 | 1 | V19 | V19 |  | uint16 | % VRef | V_SF | RW | O | Point 19 Volts.
Repeating Block |  | 51 | 39 | 1 | VAr19 | VAr19 |  | int16 |  | DeptRef_SF | RW | O | Point 19 VARs.
Repeating Block |  | 52 | 40 | 1 | V20 | V20 |  | uint16 | % VRef | V_SF | RW | O | Point 20 Volts.
Repeating Block |  | 53 | 41 | 1 | VAr20 | VAr20 |  | int16 |  | DeptRef_SF | RW | O | Point 20 VARs.
Repeating Block |  | 54 | 42 | 8 | CrvNam | CrvNam |  | string |  |  | RW | O | Optional description for curve. (Max 16 chars)
Repeating Block |  | 62 | 50 | 1 | RmpTms |  |  | uint16 | Secs |  | RW | O
Repeating Block |  | 63 | 51 | 1 | RmpDecTmm | RmpDecTmm |  | uint16 | % ref_value/min | RmpIncDec_SF | RW | O | The maximum rate at which the VAR value may be reduced in response to changes in the voltage value. %refVal is %WMax %VArMax or %VArAval depending on value of DeptRef.
Repeating Block |  | 64 | 52 | 1 | RmpIncTmm | RmpIncTmm |  | uint16 | % ref_value/min | RmpIncDec_SF | RW | O | The maximum rate at which the VAR value may be increased in response to changes in the voltage value. %refVal is %WMax %VArMax or %VArAval depending on value of DeptRef.
Repeating Block |  | 65 | 53 | 1 | ReadOnly | ReadOnly |  | enum16 |  |  | R | M | Boolean flag indicates if curve is read-only or can be modified.
bitfield16 | ModEna |  |  | Name: ENABLED; Value: 0
enum16 | DeptRef |  |  | Name: WMax; Value: 1
enum16 | DeptRef |  |  | Name: VArMax; Value: 2
enum16 | DeptRef |  |  | Name: VArAval; Value: 3
enum16 | ReadOnly |  |  | Name: READWRITE; Value: 0
enum16 | ReadOnly |  |  | Name: READONLY; Value: 1

## 127
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Freq-Watt Param | 127 | uint16 |  |  | R | M | Parameterized Frequency-Watt | Ref 3: 8.9.1.2, 8.9.4.2
Header |  | 1 |  | 1 | L |  | 10 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | WGra | WGra |  | uint16 | % PM/Hz | WGra_SF | RW | M | The slope of the reduction in the maximum allowed watts output as a function of frequency.
Fixed Block |  | 3 | 1 | 1 | HzStr | HzStr |  | int16 | Hz | HzStrStop_SF | RW | M | The frequency deviation from nominal frequency (ECPNomHz) at which a snapshot of the instantaneous power output is taken to act as the CAPPED power level (PM) and above which reduction in power output occurs.
Fixed Block |  | 4 | 2 | 1 | HzStop | HzStop |  | int16 | Hz | HzStrStop_SF | RW | M | The frequency deviation from nominal frequency (ECPNomHz) at which curtailed power output may return to normal and the cap on the power level value is removed.
Fixed Block |  | 5 | 3 | 1 | HysEna | HysEna |  | bitfield16 |  |  | RW | M | Enable hysterisis
Fixed Block |  | 6 | 4 | 1 | ModEna | ModEna |  | bitfield16 |  |  | RW | M | Is Parameterized Frequency-Watt control active.
Fixed Block |  | 7 | 5 | 1 | HzStopWGra | HzStopWGra |  | uint16 | % WMax/min | RmpIncDec_SF | RW | O | The maximum time-based rate of change at which power output returns to normal after having been capped by an over frequency event.
Fixed Block |  | 8 | 6 | 1 | WGra_SF | WGra_SF |  | sunssf |  |  | R | O | Scale factor for output gradient.
Fixed Block |  | 9 | 7 | 1 | HzStrStop_SF | HzStrStop_SF |  | sunssf |  |  | R | O | Scale factor for frequency deviations.
Fixed Block |  | 10 | 8 | 1 | RmpIncDec_SF | RmpIncDec_SF |  | sunssf |  |  | R | O | Scale factor for increment and decrement ramps.
Fixed Block |  | 11 | 9 | Size: 1; Name: Pad; Type: pad; R/W: R | O
bitfield16 | HysEna |  |  | Name: ENABLED; Value: 0
bitfield16 | ModEna |  |  | Name: ENABLED; Value: 0

## 128
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Dynamic Reactive Current | 128 | uint16 |  |  | R | M | Dynamic Reactive Current | Ref 3: 8.10.1.2; Ref 4: 12
Header |  | 1 |  | 1 | L |  | 14 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | ArGraMod | ArGraMod |  | enum16 |  |  | RW | M | Indicates if gradients trend toward zero at the edges of the deadband or trend toward zero at the center of the deadband.
Fixed Block |  | 3 | 1 | 1 | ArGraSag | ArGraSag |  | uint16 | %ARtg/%dV | ArGra_SF | RW | M | The gradient used to increase capacitive dynamic current. A value of 0 indicates no additional reactive current support.
Fixed Block |  | 4 | 2 | 1 | ArGraSwell | ArGraSwell |  | uint16 | %ARtg/%dV | ArGra_SF | RW | M | The gradient used to increase inductive dynamic current. A value of 0 indicates no additional reactive current support.
Fixed Block |  | 5 | 3 | 1 | ModEna | ModEna |  | bitfield16 |  |  | RW | M | Activate dynamic reactive current model
Fixed Block |  | 6 | 4 | 1 | FilTms | FilTms |  | uint16 | Secs |  | RW | O | The time window used to calculate the moving average voltage.
Fixed Block |  | 7 | 5 | 1 | DbVMin | DbVMin |  | uint16 | % VRef | VRefPct_SF | RW | O | The lower delta voltage limit for which negative voltage deviations less than this value no dynamic vars are produced.
Fixed Block |  | 8 | 6 | 1 | DbVMax | DbVMax |  | uint16 | % VRef | VRefPct_SF | RW | O | The upper delta voltage limit for which positive voltage deviations less than this value no dynamic current produced.
Fixed Block |  | 9 | 7 | 1 | BlkZnV | BlkZnV |  | uint16 | % VRef | VRefPct_SF | RW | O | Block zone voltage which defines a lower voltage boundary below which no dynamic current is produced.
Fixed Block |  | 10 | 8 | 1 | HysBlkZnV | HysBlkZnV |  | uint16 | % VRef | VRefPct_SF | RW | O | Hysteresis voltage used with BlkZnV.
Fixed Block |  | 11 | 9 | 1 | BlkZnTmms | BlkZnTmms |  | uint16 | mSecs |  | RW | O | Block zone time the time before which reactive current support remains active regardless of how low the voltage drops.
Fixed Block |  | 12 | 10 | 1 | HoldTmms | HoldTmms |  | uint16 | mSecs |  | RW | O | Hold time during which reactive current support continues after the average voltage has entered the dead zone.
Fixed Block |  | 13 | 11 | 1 | ArGra_SF | ArGra_SF |  | sunssf |  |  | R | M | Scale factor for the gradients.
Fixed Block |  | 14 | 12 | 1 | VRefPct_SF | VRefPct_SF |  | sunssf |  |  | R | O | Scale factor for the voltage zone and limit settings.
Fixed Block |  | 15 | 13 | Size: 1; Name: Pad; Type: pad; R/W: R | O
enum16 | ArGraMod |  |  | Name: EDGE; Value: 0
enum16 | ArGraMod |  |  | Name: CENTER; Value: 1
bitfield16 | ModEna |  |  | Name: ENABLED; Value: 0

## 129
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | LVRTD | 129 | uint16 |  |  | R | M | LVRT Must Disconnect | Ref 4: 11
Header |  | 1 |  | 1 | L |  | 10 + (RB Count * 50) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | ActCrv | ActCrv |  | uint16 |  |  | RW | M | Index of active curve. 0=no active curve.
Fixed Block |  | 3 | 1 | 1 | ModEna | ModEna |  | bitfield16 |  |  | RW | M | LVRT control mode. Enable active curve. Bitfield value.
Fixed Block |  | 4 | 2 | 1 | WinTms | WinTms |  | uint16 | Secs |  | RW | O | Time window for LVRT change. | Setting is ignored for LVRT controls.
Fixed Block |  | 5 | 3 | 1 | RvrtTms | RvrtTms |  | uint16 | Secs |  | RW | O | Timeout period for LVRT curve selection. | Setting is ignored for LVRT controls.
Fixed Block |  | 6 | 4 | 1 | RmpTms | RmpTms |  | uint16 | Secs |  | RW | O | Ramp time for moving from current mode to new mode. | Setting is ignored for LVRT controls.
Fixed Block |  | 7 | 5 | 1 | NCrv | NCrv |  | uint16 |  |  | R | M | Number of curves supported (recommend 4).
Fixed Block |  | 8 | 6 | 1 | NPt | NPt |  | uint16 |  |  | R | M | Number of curve points supported (maximumn of 20).
Fixed Block |  | 9 | 7 | 1 | Tms_SF | Tms_SF |  | sunssf |  |  | R | M | Scale factor for duration.
Fixed Block |  | 10 | 8 | 1 | V_SF | V_SF |  | sunssf |  |  | R | M | Scale factor for percent VRef.
Fixed Block |  | 11 | 9 | Size: 1; Name: Pad; Type: pad; R/W: R | O
Repeating Block |  | 12 | 0 | 1 | ActPt | ActPt |  | uint16 |  |  | RW | M | Number of active points in array.
Repeating Block |  | 13 | 1 | 1 | Tms1 | Tms1 |  | uint16 | Secs | Tms_SF | RW | M | Point 1 must disconnect duration.
Repeating Block |  | 14 | 2 | 1 | V1 | V1 |  | uint16 | % VRef | V_SF | RW | M | Point 1 must disconnect voltage.
Repeating Block |  | 15 | 3 | 1 | Tms2 | Tms2 |  | uint16 | Secs | Tms_SF | RW | O | Point 2 must disconnect duration.
Repeating Block |  | 16 | 4 | 1 | V2 | V2 |  | uint16 | % VRef | V_SF | RW | O | Point 2 must disconnect voltage.
Repeating Block |  | 17 | 5 | 1 | Tms3 | Tms3 |  | uint16 | Secs | Tms_SF | RW | O | Point 3 must disconnect duration.
Repeating Block |  | 18 | 6 | 1 | V3 | V3 |  | uint16 | % VRef | V_SF | RW | O | Point 3 must disconnect voltage.
Repeating Block |  | 19 | 7 | 1 | Tms4 | Tms4 |  | uint16 | Secs | Tms_SF | RW | O | Point 4 must disconnect duration.
Repeating Block |  | 20 | 8 | 1 | V4 | V4 |  | uint16 | % VRef | V_SF | RW | O | Point 4 must disconnect voltage.
Repeating Block |  | 21 | 9 | 1 | Tms5 | Tms5 |  | uint16 | Secs | Tms_SF | RW | O | Point 5 must disconnect duration.
Repeating Block |  | 22 | 10 | 1 | V5 | V5 |  | uint16 | % VRef | V_SF | RW | O | Point 5 must disconnect voltage.
Repeating Block |  | 23 | 11 | 1 | Tms6 | Tms6 |  | uint16 | Secs | Tms_SF | RW | O | Point 6 must disconnect duration.
Repeating Block |  | 24 | 12 | 1 | V6 | V6 |  | uint16 | % VRef | V_SF | RW | O | Point 6 must disconnect voltage.
Repeating Block |  | 25 | 13 | 1 | Tms7 | Tms7 |  | uint16 | Secs | Tms_SF | RW | O | Point 7 must disconnect duration.
Repeating Block |  | 26 | 14 | 1 | V7 | V7 |  | uint16 | % VRef | V_SF | RW | O | Point 7 must disconnect voltage.
Repeating Block |  | 27 | 15 | 1 | Tms8 | Tms8 |  | uint16 | Secs | Tms_SF | RW | O | Point 8 must disconnect duration.
Repeating Block |  | 28 | 16 | 1 | V8 | V8 |  | uint16 | % VRef | V_SF | RW | O | Point 8 must disconnect voltage.
Repeating Block |  | 29 | 17 | 1 | Tms9 | Tms9 |  | uint16 | Secs | Tms_SF | RW | O | Point 9 must disconnect duration.
Repeating Block |  | 30 | 18 | 1 | V9 | V9 |  | uint16 | % VRef | V_SF | RW | O | Point 9 must disconnect voltage.
Repeating Block |  | 31 | 19 | 1 | Tms10 | Tms10 |  | uint16 | Secs | Tms_SF | RW | O | Point 10 must disconnect duration.
Repeating Block |  | 32 | 20 | 1 | V10 | V10 |  | uint16 | % VRef | V_SF | RW | O | Point 10 must disconnect voltage.
Repeating Block |  | 33 | 21 | 1 | Tms11 | Tms11 |  | uint16 | Secs | Tms_SF | RW | O | Point 11 must disconnect duration.
Repeating Block |  | 34 | 22 | 1 | V11 | V11 |  | uint16 | % VRef | V_SF | RW | O | Point 11 must disconnect voltage.
Repeating Block |  | 35 | 23 | 1 | Tms12 | Tms12 |  | uint16 | Secs | Tms_SF | RW | O | Point 12 must disconnect duration.
Repeating Block |  | 36 | 24 | 1 | V12 | V12 |  | uint16 | % VRef | V_SF | RW | O | Point 12 must disconnect voltage.
Repeating Block |  | 37 | 25 | 1 | Tms13 | Tms13 |  | uint16 | Secs | Tms_SF | RW | O | Point 13 must disconnect duration.
Repeating Block |  | 38 | 26 | 1 | V13 | V13 |  | uint16 | % VRef | V_SF | RW | O | Point 13 must disconnect voltage.
Repeating Block |  | 39 | 27 | 1 | Tms14 | Tms14 |  | uint16 | Secs | Tms_SF | RW | O | Point 14 must disconnect duration.
Repeating Block |  | 40 | 28 | 1 | V14 | V14 |  | uint16 | % VRef | V_SF | RW | O | Point 14 must disconnect voltage.
Repeating Block |  | 41 | 29 | 1 | Tms15 | Tms15 |  | uint16 | Secs | Tms_SF | RW | O | Point 15 must disconnect duration.
Repeating Block |  | 42 | 30 | 1 | V15 | V15 |  | uint16 | % VRef | V_SF | RW | O | Point 15 must disconnect voltage.
Repeating Block |  | 43 | 31 | 1 | Tms16 | Tms16 |  | uint16 | Secs | Tms_SF | RW | O | Point 16 must disconnect duration.
Repeating Block |  | 44 | 32 | 1 | V16 | V16 |  | uint16 | % VRef | V_SF | RW | O | Point 16 must disconnect voltage.
Repeating Block |  | 45 | 33 | 1 | Tms17 | Tms17 |  | uint16 | Secs | Tms_SF | RW | O | Point 17 must disconnect duration.
Repeating Block |  | 46 | 34 | 1 | V17 | V17 |  | uint16 | % VRef | V_SF | RW | O | Point 17 must disconnect voltage.
Repeating Block |  | 47 | 35 | 1 | Tms18 | Tms18 |  | uint16 | Secs | Tms_SF | RW | O | Point 18 must disconnect duration.
Repeating Block |  | 48 | 36 | 1 | V18 | V18 |  | uint16 | % VRef | V_SF | RW | O | Point 18 must disconnect voltage.
Repeating Block |  | 49 | 37 | 1 | Tms19 | Tms19 |  | uint16 | Secs | Tms_SF | RW | O | Point 19 must disconnect duration.
Repeating Block |  | 50 | 38 | 1 | V19 | V19 |  | uint16 | % VRef | V_SF | RW | O | Point 19 must disconnect voltage.
Repeating Block |  | 51 | 39 | 1 | Tms20 | Tms20 |  | uint16 | Secs | Tms_SF | RW | O | Point 20 must disconnect duration.
Repeating Block |  | 52 | 40 | 1 | V20 | V20 |  | uint16 | % VRef | V_SF | RW | O | Point 20 must disconnect voltage.
Repeating Block |  | 53 | 41 | 8 | CrvNam | CrvNam |  | string |  |  | RW | O | Optional description for curve.
Repeating Block |  | 61 | 49 | 1 | ReadOnly | ReadOnly |  | enum16 |  |  | R | M | Enumerated value indicates if curve is read-only or can be modified.
bitfield16 | ModEna |  |  | Name: ENABLED; Value: 0
enum16 | ReadOnly |  |  | Name: READWRITE; Value: 0
enum16 | ReadOnly |  |  | Name: READONLY; Value: 1

## 130
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | HVRTD | 130 | uint16 |  |  | R | M | HVRT Must Disconnect | Ref 4: 11
Header |  | 1 |  | 1 | L |  | 10 + (RB Count * 50) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | ActCrv | ActCrv |  | uint16 |  |  | RW | M | Index of active curve. 0=no active curve.
Fixed Block |  | 3 | 1 | 1 | ModEna | ModEna |  | bitfield16 |  |  | RW | M | HVRT control mode. Enable active curve. Bitfield value.
Fixed Block |  | 4 | 2 | 1 | WinTms | WinTms |  | uint16 | Secs |  | RW | O | Time window for HVRT change. | Setting is ignored for HVRT controls.
Fixed Block |  | 5 | 3 | 1 | RvrtTms | RvrtTms |  | uint16 | Secs |  | RW | O | Timeout period for HVRT curve selection. | Setting is ignored for HVRT controls.
Fixed Block |  | 6 | 4 | 1 | RmpTms | RmpTms |  | uint16 | Secs |  | RW | O | Ramp time for moving from current mode to new mode. | Setting is ignored for HVRT controls.
Fixed Block |  | 7 | 5 | 1 | NCrv | NCrv |  | uint16 |  |  | R | M | Number of curves supported (recommend 4).
Fixed Block |  | 8 | 6 | 1 | NPt | NPt |  | uint16 |  |  | R | M | Number of curve points supported (maximumn of 20).
Fixed Block |  | 9 | 7 | 1 | Tms_SF | Tms_SF |  | sunssf |  |  | R | M | Scale factor for duration.
Fixed Block |  | 10 | 8 | 1 | V_SF | V_SF |  | sunssf |  |  | R | M | Scale factor for percent VRef.
Fixed Block |  | 11 | 9 | Size: 1; Name: Pad; Type: pad; R/W: R | O
Repeating Block |  | 12 | 0 | 1 | ActPt | ActPt |  | uint16 |  |  | RW | M | Number of active points in array.
Repeating Block |  | 13 | 1 | 1 | Tms1 | Tms1 |  | uint16 | Secs | Tms_SF | RW | M | Point 1 must disconnect duration.
Repeating Block |  | 14 | 2 | 1 | V1 | V1 |  | uint16 | % VRef | V_SF | RW | M | Point 1 must disconnect voltage.
Repeating Block |  | 15 | 3 | 1 | Tms2 | Tms2 |  | uint16 | Secs | Tms_SF | RW | O | Point 2 must disconnect duration.
Repeating Block |  | 16 | 4 | 1 | V2 | V2 |  | uint16 | % VRef | V_SF | RW | O | Point 2 must disconnect voltage.
Repeating Block |  | 17 | 5 | 1 | Tms3 | Tms3 |  | uint16 | Secs | Tms_SF | RW | O | Point 3 must disconnect duration.
Repeating Block |  | 18 | 6 | 1 | V3 | V3 |  | uint16 | % VRef | V_SF | RW | O | Point 3 must disconnect voltage.
Repeating Block |  | 19 | 7 | 1 | Tms4 | Tms4 |  | uint16 | Secs | Tms_SF | RW | O | Point 4 must disconnect duration.
Repeating Block |  | 20 | 8 | 1 | V4 | V4 |  | uint16 | % VRef | V_SF | RW | O | Point 4 must disconnect voltage.
Repeating Block |  | 21 | 9 | 1 | Tms5 | Tms5 |  | uint16 | Secs | Tms_SF | RW | O | Point 5 must disconnect duration.
Repeating Block |  | 22 | 10 | 1 | V5 | V5 |  | uint16 | % VRef | V_SF | RW | O | Point 5 must disconnect voltage.
Repeating Block |  | 23 | 11 | 1 | Tms6 | Tms6 |  | uint16 | Secs | Tms_SF | RW | O | Point 6 must disconnect duration.
Repeating Block |  | 24 | 12 | 1 | V6 | V6 |  | uint16 | % VRef | V_SF | RW | O | Point 6 must disconnect voltage.
Repeating Block |  | 25 | 13 | 1 | Tms7 | Tms7 |  | uint16 | Secs | Tms_SF | RW | O | Point 7 must disconnect duration.
Repeating Block |  | 26 | 14 | 1 | V7 | V7 |  | uint16 | % VRef | V_SF | RW | O | Point 7 must disconnect voltage.
Repeating Block |  | 27 | 15 | 1 | Tms8 | Tms8 |  | uint16 | Secs | Tms_SF | RW | O | Point 8 must disconnect duration.
Repeating Block |  | 28 | 16 | 1 | V8 | V8 |  | uint16 | % VRef | V_SF | RW | O | Point 8 must disconnect voltage.
Repeating Block |  | 29 | 17 | 1 | Tms9 | Tms9 |  | uint16 | Secs | Tms_SF | RW | O | Point 9 must disconnect duration.
Repeating Block |  | 30 | 18 | 1 | V9 | V9 |  | uint16 | % VRef | V_SF | RW | O | Point 9 must disconnect voltage.
Repeating Block |  | 31 | 19 | 1 | Tms10 | Tms10 |  | uint16 | Secs | Tms_SF | RW | O | Point 10 must disconnect duration.
Repeating Block |  | 32 | 20 | 1 | V10 | V10 |  | uint16 | % VRef | V_SF | RW | O | Point 10 must disconnect voltage.
Repeating Block |  | 33 | 21 | 1 | Tms11 | Tms11 |  | uint16 | Secs | Tms_SF | RW | O | Point 11 must disconnect duration.
Repeating Block |  | 34 | 22 | 1 | V11 | V11 |  | uint16 | % VRef | V_SF | RW | O | Point 11 must disconnect voltage.
Repeating Block |  | 35 | 23 | 1 | Tms12 | Tms12 |  | uint16 | Secs | Tms_SF | RW | O | Point 12 must disconnect duration.
Repeating Block |  | 36 | 24 | 1 | V12 | V12 |  | uint16 | % VRef | V_SF | RW | O | Point 12 must disconnect voltage.
Repeating Block |  | 37 | 25 | 1 | Tms13 | Tms13 |  | uint16 | Secs | Tms_SF | RW | O | Point 13 must disconnect duration.
Repeating Block |  | 38 | 26 | 1 | V13 | V13 |  | uint16 | % VRef | V_SF | RW | O | Point 13 must disconnect voltage.
Repeating Block |  | 39 | 27 | 1 | Tms14 | Tms14 |  | uint16 | Secs | Tms_SF | RW | O | Point 14 must disconnect duration.
Repeating Block |  | 40 | 28 | 1 | V14 | V14 |  | uint16 | % VRef | V_SF | RW | O | Point 14 must disconnect voltage.
Repeating Block |  | 41 | 29 | 1 | Tms15 | Tms15 |  | uint16 | Secs | Tms_SF | RW | O | Point 15 must disconnect duration.
Repeating Block |  | 42 | 30 | 1 | V15 | V15 |  | uint16 | % VRef | V_SF | RW | O | Point 15 must disconnect voltage.
Repeating Block |  | 43 | 31 | 1 | Tms16 | Tms16 |  | uint16 | Secs | Tms_SF | RW | O | Point 16 must disconnect duration.
Repeating Block |  | 44 | 32 | 1 | V16 | V16 |  | uint16 | % VRef | V_SF | RW | O | Point 16 must disconnect voltage.
Repeating Block |  | 45 | 33 | 1 | Tms17 | Tms17 |  | uint16 | Secs | Tms_SF | RW | O | Point 17 must disconnect duration.
Repeating Block |  | 46 | 34 | 1 | V17 | V17 |  | uint16 | % VRef | V_SF | RW | O | Point 17 must disconnect voltage.
Repeating Block |  | 47 | 35 | 1 | Tms18 | Tms18 |  | uint16 | Secs | Tms_SF | RW | O | Point 18 must disconnect duration.
Repeating Block |  | 48 | 36 | 1 | V18 | V18 |  | uint16 | % VRef | V_SF | RW | O | Point 18 must disconnect voltage.
Repeating Block |  | 49 | 37 | 1 | Tms19 | Tms19 |  | uint16 | Secs | Tms_SF | RW | O | Point 19 must disconnect duration.
Repeating Block |  | 50 | 38 | 1 | V19 | V19 |  | uint16 | % VRef | V_SF | RW | O | Point 19 must disconnect voltage.
Repeating Block |  | 51 | 39 | 1 | Tms20 | Tms20 |  | uint16 | Secs | Tms_SF | RW | O | Point 20 must disconnect duration.
Repeating Block |  | 52 | 40 | 1 | V20 | V20 |  | uint16 | % VRef | V_SF | RW | O | Point 20 must disconnect voltage.
Repeating Block |  | 53 | 41 | 8 | CrvNam | CrvNam |  | string |  |  | RW | O | Optional description for curve.
Repeating Block |  | 61 | 49 | 1 | ReadOnly | ReadOnly |  | enum16 |  |  | R | M | Enumerated value indicates if curve is read-only or can be modified.
bitfield16 | ModEna |  |  | Name: ENABLED; Value: 0
enum16 | ReadOnly |  |  | Name: READWRITE; Value: 0
enum16 | ReadOnly |  |  | Name: READONLY; Value: 1

## 131
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Watt-PF | 131 | uint16 |  |  | R | M | Watt-Power Factor | Ref 3: 8.11.1.2
Header |  | 1 |  | 1 | L |  | 10 + (RB Count * 54) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | ActCrv | ActCrv |  | uint16 |  |  | RW | M | Index of active curve. 0=no active curve.
Fixed Block |  | 3 | 1 | 1 | ModEna | ModEna |  | bitfield16 |  |  | RW | M | Is watt-PF mode active.
Fixed Block |  | 4 | 2 | 1 | WinTms | WinTms |  | uint16 | Secs |  | RW | O | Time window for watt-PF change.
Fixed Block |  | 5 | 3 | 1 | RvrtTms | RvrtTms |  | uint16 | Secs |  | RW | O | Timeout period for watt-PF curve selection.
Fixed Block |  | 6 | 4 | 1 | RmpTms | RmpTms |  | uint16 | Secs |  | RW | O | Ramp time for moving from current mode to new mode.
Fixed Block |  | 7 | 5 | 1 | NCrv | NCrv |  | uint16 |  |  | R | M | Number of curves supported (recommend 4).
Fixed Block |  | 8 | 6 | 1 | NPt | NPt |  | uint16 |  |  | R | M | Max number of points in array.
Fixed Block |  | 9 | 7 | 1 | W_SF | W_SF |  | sunssf |  |  | R | M | Scale factor for percent WMax.
Fixed Block |  | 10 | 8 | 1 | PF_SF | PF_SF |  | sunssf |  |  | R | M | Scale factor for PF.
Fixed Block |  | 11 | 9 | 1 | RmpIncDec_SF | RmpIncDec_SF |  | sunssf |  |  | R | O | Scale factor for increment and decrement ramps.
Repeating Block |  | 12 | 0 | 1 | ActPt | ActPt |  | uint16 |  |  | RW | M | Number of active points in array.
Repeating Block |  | 13 | 1 | 1 | W1 | W1 |  | int16 | % WMax | W_SF | RW | M | Point 1 Watts.
Repeating Block |  | 14 | 2 | 1 | PF1 | PF1 |  | int16 | cos() | PF_SF | RW | M | Point 1 PF in EEI notation.
Repeating Block |  | 15 | 3 | 1 | W2 | W2 |  | int16 | % WMax | W_SF | RW | O | Point 2 Watts.
Repeating Block |  | 16 | 4 | 1 | PF2 | PF2 |  | int16 | cos() | PF_SF | RW | O | Point 2 PF in EEI notation.
Repeating Block |  | 17 | 5 | 1 | W3 | W3 |  | int16 | % WMax | W_SF | RW | O | Point 3 Watts.
Repeating Block |  | 18 | 6 | 1 | PF3 | PF3 |  | int16 | cos() | PF_SF | RW | O | Point 3 PF in EEI notation.
Repeating Block |  | 19 | 7 | 1 | W4 | W4 |  | int16 | % WMax | W_SF | RW | O | Point 4 Watts.
Repeating Block |  | 20 | 8 | 1 | PF4 | PF4 |  | int16 | cos() | PF_SF | RW | O | Point 4 PF in EEI notation.
Repeating Block |  | 21 | 9 | 1 | W5 | W5 |  | int16 | % WMax | W_SF | RW | O | Point 5 Watts.
Repeating Block |  | 22 | 10 | 1 | PF5 | PF5 |  | int16 | cos() | PF_SF | RW | O | Point 5 PF in EEI notation.
Repeating Block |  | 23 | 11 | 1 | W6 | W6 |  | int16 | % WMax | W_SF | RW | O | Point 6 Watts.
Repeating Block |  | 24 | 12 | 1 | PF6 | PF6 |  | int16 | cos() | PF_SF | RW | O | Point 6 PF in EEI notation.
Repeating Block |  | 25 | 13 | 1 | W7 | W7 |  | int16 | % WMax | W_SF | RW | O | Point 7 Watts.
Repeating Block |  | 26 | 14 | 1 | PF7 | PF7 |  | int16 | cos() | PF_SF | RW | O | Point 7 PF in EEI notation.
Repeating Block |  | 27 | 15 | 1 | W8 | W8 |  | int16 | % WMax | W_SF | RW | O | Point 8 Watts.
Repeating Block |  | 28 | 16 | 1 | PF8 | PF8 |  | int16 | cos() | PF_SF | RW | O | Point 8 PF in EEI notation.
Repeating Block |  | 29 | 17 | 1 | W9 | W9 |  | int16 | % WMax | W_SF | RW | O | Point 9 Watts.
Repeating Block |  | 30 | 18 | 1 | PF9 | PF9 |  | int16 | cos() | PF_SF | RW | O | Point 9 PF in EEI notation.
Repeating Block |  | 31 | 19 | 1 | W10 | W10 |  | int16 | % WMax | W_SF | RW | O | Point 10 Watts.
Repeating Block |  | 32 | 20 | 1 | PF10 | PF10 |  | int16 | cos() | PF_SF | RW | O | Point 10 PF in EEI notation.
Repeating Block |  | 33 | 21 | 1 | W11 | W11 |  | int16 | % WMax | W_SF | RW | O | Point 11 Watts.
Repeating Block |  | 34 | 22 | 1 | PF11 | PF11 |  | int16 | cos() | PF_SF | RW | O | Point 11 PF in EEI notation.
Repeating Block |  | 35 | 23 | 1 | W12 | W12 |  | int16 | % WMax | W_SF | RW | O | Point 12 Watts.
Repeating Block |  | 36 | 24 | 1 | PF12 | PF12 |  | int16 | cos() | PF_SF | RW | O | Point 12 PF in EEI notation.
Repeating Block |  | 37 | 25 | 1 | W13 | W13 |  | int16 | % WMax | W_SF | RW | O | Point 13 Watts.
Repeating Block |  | 38 | 26 | 1 | PF13 | PF13 |  | int16 | cos() | PF_SF | RW | O | Point 13 PF in EEI notation.
Repeating Block |  | 39 | 27 | 1 | W14 | W14 |  | int16 | % WMax | W_SF | RW | O | Point 14 Watts.
Repeating Block |  | 40 | 28 | 1 | PF14 | PF14 |  | int16 | cos() | PF_SF | RW | O | Point 14 PF in EEI notation.
Repeating Block |  | 41 | 29 | 1 | W15 | W15 |  | int16 | % WMax | W_SF | RW | O | Point 15 Watts.
Repeating Block |  | 42 | 30 | 1 | PF15 | PF15 |  | int16 | cos() | PF_SF | RW | O | Point 15 PF in EEI notation.
Repeating Block |  | 43 | 31 | 1 | W16 | W16 |  | int16 | % WMax | W_SF | RW | O | Point 16 Watts.
Repeating Block |  | 44 | 32 | 1 | PF16 | PF16 |  | int16 | cos() | PF_SF | RW | O | Point 16 PF in EEI notation.
Repeating Block |  | 45 | 33 | 1 | W17 | W17 |  | int16 | % WMax | W_SF | RW | O | Point 17 Watts.
Repeating Block |  | 46 | 34 | 1 | PF17 | PF17 |  | int16 | cos() | PF_SF | RW | O | Point 17 PF in EEI notation.
Repeating Block |  | 47 | 35 | 1 | W18 | W18 |  | int16 | % WMax | W_SF | RW | O | Point 18 Watts.
Repeating Block |  | 48 | 36 | 1 | PF18 | PF18 |  | int16 | cos() | PF_SF | RW | O | Point 18 PF in EEI notation.
Repeating Block |  | 49 | 37 | 1 | W19 | W19 |  | int16 | % WMax | W_SF | RW | O | Point 19 Watts.
Repeating Block |  | 50 | 38 | 1 | PF19 | PF19 |  | int16 | cos() | PF_SF | RW | O | Point 19 PF in EEI notation.
Repeating Block |  | 51 | 39 | 1 | W20 | W20 |  | int16 | % WMax | W_SF | RW | O | Point 20 Watts.
Repeating Block |  | 52 | 40 | 1 | PF20 | PF20 |  | int16 | cos() | PF_SF | RW | O | Point 20 PF in EEI notation.
Repeating Block |  | 53 | 41 | 8 | CrvNam | CrvNam |  | string |  |  | RW | O | Optional description for curve.
Repeating Block |  | 61 | 49 | 1 | RmpPT1Tms | RmpPT1Tms |  | uint16 | Secs |  | RW | O | The time of the PT1 in seconds (time to accomplish a change of 95%).
Repeating Block |  | 62 | 50 | 1 | RmpDecTmm | RmpDecTmm |  | uint16 | % PF/min | RmpIncDec_SF | RW | O | The maximum rate at which the power factor may be reduced in response to changes in the power value.
Repeating Block |  | 63 | 51 | 1 | RmpIncTmm | RmpIncTmm |  | uint16 | % PF/min | RmpIncDec_SF | RW | O | The maximum rate at which the power factor may be increased in response to changes in the power value.
Repeating Block |  | 64 | 52 | 1 | ReadOnly | ReadOnly |  | enum16 |  |  | R | M | Enumerated value indicates if curve is read-only or can be modified.
Repeating Block |  | 65 | 53 | Size: 1; Name: Pad; Type: pad; R/W: R | O
bitfield16 | ModEna |  |  | Name: ENABLED; Value: 0
enum16 | ReadOnly |  |  | Name: READWRITE; Value: 0
enum16 | ReadOnly |  |  | Name: READONLY; Value: 1

## 132
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Volt-Watt | 132 | uint16 |  |  | R | M | Volt-Watt | Ref 3: 8.12.1.2
Header |  | 1 |  | 1 | L |  | 10 + (RB Count * 54) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | ActCrv | ActCrv |  | uint16 |  |  | RW | M | Index of active curve. 0=no active curve.
Fixed Block |  | 3 | 1 | 1 | ModEna | ModEna |  | bitfield16 |  |  | RW | M | Is Volt-Watt control active.
Fixed Block |  | 4 | 2 | 1 | WinTms | WinTms |  | uint16 | Secs |  | RW | O | Time window for volt-watt change.
Fixed Block |  | 5 | 3 | 1 | RvrtTms | RvrtTms |  | uint16 | Secs |  | RW | O | Timeout period for volt-watt curve selection.
Fixed Block |  | 6 | 4 | 1 | RmpTms | RmpTms |  | uint16 | Secs |  | RW | O | Ramp time for moving from current mode to new mode.
Fixed Block |  | 7 | 5 | 1 | NCrv | NCrv |  | uint16 |  |  | R | M | Number of curves supported (recommend min. 4).
Fixed Block |  | 8 | 6 | 1 | NPt | NPt |  | uint16 |  |  | R | M | Number of points in array (maximum 20).
Fixed Block |  | 9 | 7 | 1 | V_SF | V_SF |  | sunssf |  |  | R | M | Scale factor for percent VRef.
Fixed Block |  | 10 | 8 | 1 | DeptRef_SF | DeptRef_SF |  | sunssf |  |  | R | M | Scale Factor for % DeptRef
Fixed Block |  | 11 | 9 | 1 | RmpIncDec_SF | RmpIncDec_SF |  | sunssf |  |  | R | O | Scale factor for increment and decrement ramps.
Repeating Block |  | 12 | 0 | 1 | ActPt | ActPt |  | uint16 |  |  | RW | M | Number of active points in array.
Repeating Block |  | 13 | 1 | 1 | DeptRef | DeptRef |  | enum16 |  |  | RW | M | Defines the meaning of the Watts DeptRef. 1=% WMax 2=% WAvail
Repeating Block |  | 14 | 2 | 1 | V1 | V1 |  | uint16 | % VRef | V_SF | RW | M | Point 1 Volts.
Repeating Block |  | 15 | 3 | 1 | W1 | W1 |  | int16 | % VRef | DeptRef_SF | RW | M | Point 1 Watts.
Repeating Block |  | 16 | 4 | 1 | V2 | V2 |  | uint16 | % VRef | V_SF | RW | O | Point 2 Volts.
Repeating Block |  | 17 | 5 | 1 | W2 | W2 |  | int16 | % VRef | DeptRef_SF | RW | O | Point 2 Watts.
Repeating Block |  | 18 | 6 | 1 | V3 | V3 |  | uint16 | % VRef | V_SF | RW | O | Point 3 Volts.
Repeating Block |  | 19 | 7 | 1 | W3 | W3 |  | int16 | % VRef | DeptRef_SF | RW | O | Point 3 Watts.
Repeating Block |  | 20 | 8 | 1 | V4 | V4 |  | uint16 | % VRef | V_SF | RW | O | Point 4 Volts.
Repeating Block |  | 21 | 9 | 1 | W4 | W4 |  | int16 | % VRef | DeptRef_SF | RW | O | Point 4 Watts.
Repeating Block |  | 22 | 10 | 1 | V5 | V5 |  | uint16 | % VRef | V_SF | RW | O | Point 5 Volts.
Repeating Block |  | 23 | 11 | 1 | W5 | W5 |  | int16 | % VRef | DeptRef_SF | RW | O | Point 5 Watts.
Repeating Block |  | 24 | 12 | 1 | V6 | V6 |  | uint16 | % VRef | V_SF | RW | O | Point 6 Volts.
Repeating Block |  | 25 | 13 | 1 | W6 | W6 |  | int16 | % VRef | DeptRef_SF | RW | O | Point 6 Watts.
Repeating Block |  | 26 | 14 | 1 | V7 | V7 |  | uint16 | % VRef | V_SF | RW | O | Point 7 Volts.
Repeating Block |  | 27 | 15 | 1 | W7 | W7 |  | int16 | % VRef | DeptRef_SF | RW | O | Point 7 Watts.
Repeating Block |  | 28 | 16 | 1 | V8 | V8 |  | uint16 | % VRef | V_SF | RW | O | Point 8 Volts.
Repeating Block |  | 29 | 17 | 1 | W8 | W8 |  | int16 | % VRef | DeptRef_SF | RW | O | Point 8 Watts.
Repeating Block |  | 30 | 18 | 1 | V9 | V9 |  | uint16 | % VRef | V_SF | RW | O | Point 9 Volts.
Repeating Block |  | 31 | 19 | 1 | W9 | W9 |  | int16 | % VRef | DeptRef_SF | RW | O | Point 9 Watts.
Repeating Block |  | 32 | 20 | 1 | V10 | V10 |  | uint16 | % VRef | V_SF | RW | O | Point 10 Volts.
Repeating Block |  | 33 | 21 | 1 | W10 | W10 |  | int16 | % VRef | DeptRef_SF | RW | O | Point 10 Watts.
Repeating Block |  | 34 | 22 | 1 | V11 | V11 |  | uint16 | % VRef | V_SF | RW | O | Point 11 Volts.
Repeating Block |  | 35 | 23 | 1 | W11 | W11 |  | int16 | % VRef | DeptRef_SF | RW | O | Point 11 Watts.
Repeating Block |  | 36 | 24 | 1 | V12 | V12 |  | uint16 | % VRef | V_SF | RW | O | Point 12 Volts.
Repeating Block |  | 37 | 25 | 1 | W12 | W12 |  | int16 | % VRef | DeptRef_SF | RW | O | Point 12 Watts.
Repeating Block |  | 38 | 26 | 1 | V13 | V13 |  | uint16 | % VRef | V_SF | RW | O | Point 13 Volts.
Repeating Block |  | 39 | 27 | 1 | W13 | W13 |  | int16 | % VRef | DeptRef_SF | RW | O | Point 13 Watts.
Repeating Block |  | 40 | 28 | 1 | V14 | V14 |  | uint16 | % VRef | V_SF | RW | O | Point 14 Volts.
Repeating Block |  | 41 | 29 | 1 | W14 | W14 |  | int16 | % VRef | DeptRef_SF | RW | O | Point 14 Watts.
Repeating Block |  | 42 | 30 | 1 | V15 | V15 |  | uint16 | % VRef | V_SF | RW | O | Point 15 Volts.
Repeating Block |  | 43 | 31 | 1 | W15 | W15 |  | int16 | % VRef | DeptRef_SF | RW | O | Point 15 Watts.
Repeating Block |  | 44 | 32 | 1 | V16 | V16 |  | uint16 | % VRef | V_SF | RW | O | Point 16 Volts.
Repeating Block |  | 45 | 33 | 1 | W16 | W16 |  | int16 | % VRef | DeptRef_SF | RW | O | Point 16 Watts.
Repeating Block |  | 46 | 34 | 1 | V17 | V17 |  | uint16 | % VRef | V_SF | RW | O | Point 17 Volts.
Repeating Block |  | 47 | 35 | 1 | W17 | W17 |  | int16 | % VRef | DeptRef_SF | RW | O | Point 17 Watts.
Repeating Block |  | 48 | 36 | 1 | V18 | V18 |  | uint16 | % VRef | V_SF | RW | O | Point 18 Volts.
Repeating Block |  | 49 | 37 | 1 | W18 | W18 |  | int16 | % VRef | DeptRef_SF | RW | O | Point 18 Watts.
Repeating Block |  | 50 | 38 | 1 | V19 | V19 |  | uint16 | % VRef | V_SF | RW | O | Point 19 Volts.
Repeating Block |  | 51 | 39 | 1 | W19 | W19 |  | int16 | % VRef | DeptRef_SF | RW | O | Point 19 Watts.
Repeating Block |  | 52 | 40 | 1 | V20 | V20 |  | uint16 | % VRef | V_SF | RW | O | Point 20 Volts.
Repeating Block |  | 53 | 41 | 1 | W20 | W20 |  | int16 | % VRef | DeptRef_SF | RW | O | Point 20 Watts.
Repeating Block |  | 54 | 42 | 8 | CrvNam | CrvNam |  | string |  |  | RW | O | Optional description for curve.
Repeating Block |  | 62 | 50 | 1 | RmpPt1Tms | RmpPt1Tms |  | uint16 | Secs |  | RW | O | The time of the PT1 in seconds (time to accomplish a change of 95%).
Repeating Block |  | 63 | 51 | 1 | RmpDecTmm | RmpDecTmm |  | uint16 | % WMax/min | RmpIncDec_SF | RW | O | The maximum rate at which the watt value may be reduced in response to changes in the voltage value.
Repeating Block |  | 64 | 52 | 1 | RmpIncTmm | RmpIncTmm |  | uint16 | % WMax/min | RmpIncDec_SF | RW | O | The maximum rate at which the watt value may be increased in response to changes in the voltage value.
Repeating Block |  | 65 | 53 | 1 | ReadOnly | ReadOnly |  | enum16 |  |  | R | M | Enumerated value indicates if curve is read-only or can be modified.
bitfield16 | ModEna |  |  | Name: ENABLED; Value: 0
enum16 | DeptRef |  |  | Name: %WMax; Value: 1
enum16 | DeptRef |  |  | Name: %WAval; Value: 2
enum16 | ReadOnly |  |  | Name: READWRITE; Value: 0
enum16 | ReadOnly |  |  | Name: READONLY; Value: 1

## 133
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Basic Scheduling | 133 | uint16 |  |  | R | M | Basic Scheduling | Ref 2: 2.2.8
Header |  | 1 |  | 1 | L |  | 6 + (RB Count * 60) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 2 | ActSchd | ActSchd |  | bitfield32 |  |  | RW | M | Bitfield of active schedules
Fixed Block |  | 4 | 2 | 1 | ModEna | ModEna |  | bitfield16 |  |  | RW | M | Is basic scheduling active.
Fixed Block |  | 5 | 3 | 1 | NSchd | NSchd |  | uint16 |  |  | R | M | Number of schedules supported (recommend min. 4, max 32)
Fixed Block |  | 6 | 4 | 1 | NPts | NPts |  | uint16 |  |  | R | M | Number of schedule entries supuported (maximum of 10).
Fixed Block |  | 7 | 5 | 1 | Pad | Pad |  | pad |  |  | R | O | Pad register.
Repeating Block |  | 8 | 0 | 1 | ActPts | ActPts |  | uint16 |  |  | RW | M | Number of active entries in schedule.
Repeating Block |  | 9 | 1 | 2 | StrTms | StrTms |  | uint32 | Secs |  | RW | M | Schedule start in seconds since 2000 JAN 01 00:00:00 UTC.
Repeating Block |  | 11 | 3 | 1 | RepPer | RepPer |  | uint16 |  |  | RW | M | The repetition count for time-based schedules (0=repeat forever)
Repeating Block |  | 12 | 4 | 1 | IntvTyp | SchdTyp |  | enum16 |  |  | RW | M | The repetition frequency for time-based schedules: no repeat=0
Repeating Block |  | 13 | 5 | 1 | XTyp | XTyp |  | enum16 |  |  | RW | M | The meaning of the X-values in the array.
Repeating Block |  | 14 | 6 | 1 | X_SF | X_SF |  | sunssf |  |  | RW | M | Scale factor for schedule range values.
Repeating Block |  | 15 | 7 | 1 | YTyp | YTyp |  | enum16 |  |  | RW | M | The meaning of the Y-values in the array.
Repeating Block |  | 16 | 8 | 1 | Y_SF | Y_SF |  | sunssf |  |  | RW | M | Scale factor for schedule target values.
Repeating Block |  | 17 | 9 | 2 | X1 | X1 |  | int32 |  | X_SF | RW | M | Entry 1 range.
Repeating Block |  | 19 | 11 | 2 | Y1 | Y1 |  | int32 |  | Y_SF | RW | M | Entry 1 target.
Repeating Block |  | 21 | 13 | 2 | X2 | X2 |  | int32 |  | X_SF | RW | O | Entry 2 range.
Repeating Block |  | 23 | 15 | 2 | Y2 | Y2 |  | int32 |  | Y_SF | RW | O | Entry 2 target.
Repeating Block |  | 25 | 17 | 2 | X3 | X3 |  | int32 |  | X_SF | RW | O | Entry 3 range.
Repeating Block |  | 27 | 19 | 2 | Y3 | Y3 |  | int32 |  | Y_SF | RW | O | Entry 3 target.
Repeating Block |  | 29 | 21 | 2 | X4 | X4 |  | int32 |  | X_SF | RW | O | Entry 4 range.
Repeating Block |  | 31 | 23 | 2 | Y4 | Y4 |  | int32 |  | Y_SF | RW | O | Entry 4 target.
Repeating Block |  | 33 | 25 | 2 | X5 | X5 |  | int32 |  | X_SF | RW | O | Entry 15range.
Repeating Block |  | 35 | 27 | 2 | Y5 | Y5 |  | int32 |  | Y_SF | RW | O | Entry 5 target.
Repeating Block |  | 37 | 29 | 2 | X6 | X6 |  | int32 |  | X_SF | RW | O | Entry 6 range.
Repeating Block |  | 39 | 31 | 2 | Y6 | Y6 |  | int32 |  | Y_SF | RW | O | Entry 6 target.
Repeating Block |  | 41 | 33 | 2 | X7 | X7 |  | int32 |  | X_SF | RW | O | Entry 7 range.
Repeating Block |  | 43 | 35 | 2 | Y7 | Y7 |  | int32 |  | Y_SF | RW | O | Entry 7 target.
Repeating Block |  | 45 | 37 | 2 | X8 | X8 |  | int32 |  | X_SF | RW | O | Entry 8 range.
Repeating Block |  | 47 | 39 | 2 | Y8 | Y8 |  | int32 |  | Y_SF | RW | O | Entry 8 target.
Repeating Block |  | 49 | 41 | 2 | X9 | X9 |  | int32 |  | X_SF | RW | O | Entry 9 range.
Repeating Block |  | 51 | 43 | 2 | Y9 | Y9 |  | int32 |  | Y_SF | RW | O | Entry 9 target.
Repeating Block |  | 53 | 45 | 2 | X10 | X10 |  | int32 |  | X_SF | RW | O | Entry 10 range.
Repeating Block |  | 55 | 47 | 2 | Y10 | Y10 |  | int32 |  | Y_SF | RW | O | Entry 10 target.
Repeating Block |  | 57 | 49 | 8 | Nam | Nam |  | string |  |  | RW | O | Optional description for schedule.
Repeating Block |  | 65 | 57 | 1 | WinTms | WinTms |  | uint16 | Secs |  | RW | O | Time window for schedule entry change.
Repeating Block |  | 66 | 58 | 1 | RmpTms | RmpTms |  | uint16 | Secs |  | RW | O | Ramp time for moving from current target to new target.
Repeating Block |  | 67 | 59 | 1 | ActIndx | ActIndx |  | uint16 |  |  | R | M | Index of active entry in the active schedule.
bitfield32 | ActSchd |  |  | Name: SCHED1; Value: 0
bitfield32 | ActSchd |  |  | Name: SCHED2; Value: 1
bitfield32 | ActSchd |  |  | Name: SCHED3; Value: 2
bitfield32 | ActSchd |  |  | Name: SCHED4; Value: 3
bitfield32 | ActSchd |  |  | Name: SCHED5; Value: 4
bitfield32 | ActSchd |  |  | Name: SCHED6; Value: 5
bitfield32 | ActSchd |  |  | Name: SCHED7; Value: 6
bitfield32 | ActSchd |  |  | Name: SCHED8; Value: 7
bitfield32 | ActSchd |  |  | Name: SCHED9; Value: 8
bitfield32 | ActSchd |  |  | Name: SCHED10; Value: 9
bitfield32 | ActSchd |  |  | Name: SCHED12; Value: 10
bitfield32 | ActSchd |  |  | Name: SCHED13; Value: 11
bitfield32 | ActSchd |  |  | Name: SCHED14; Value: 12
bitfield32 | ActSchd |  |  | Name: SCHED15; Value: 13
bitfield32 | ActSchd |  |  | Name: SCHED16; Value: 14
bitfield32 | ActSchd |  |  | Name: SCHED17; Value: 15
bitfield32 | ActSchd |  |  | Name: SCHED18; Value: 16
bitfield32 | ActSchd |  |  | Name: SCHED19; Value: 17
bitfield32 | ActSchd |  |  | Name: SCHED20; Value: 18
bitfield32 | ActSchd |  |  | Name: SCHED21; Value: 19
bitfield32 | ActSchd |  |  | Name: SCHED22; Value: 21
bitfield32 | ActSchd |  |  | Name: SCHED23; Value: 22
bitfield32 | ActSchd |  |  | Name: SCHED24; Value: 23
bitfield32 | ActSchd |  |  | Name: SCHED25; Value: 24
bitfield32 | ActSchd |  |  | Name: SCHED26; Value: 25
bitfield32 | ActSchd |  |  | Name: SCHED27; Value: 26
bitfield32 | ActSchd |  |  | Name: SCHED28; Value: 27
bitfield32 | ActSchd |  |  | Name: SCHED29; Value: 28
bitfield32 | ActSchd |  |  | Name: SCHED30; Value: 29
bitfield32 | ActSchd |  |  | Name: SCHED31; Value: 30
bitfield32 | ActSchd |  |  | Name: SCHED32; Value: 31
bitfield16 | ModEna |  |  | Name: ENABLED; Value: 0
enum16 | IntvTyp |  |  | Name: ONETIME; Value: 0
enum16 | IntvTyp |  |  | Name: DAILY; Value: 1
enum16 | IntvTyp |  |  | Name: WEEKLY; Value: 2
enum16 | IntvTyp |  |  | Name: MONTHLY; Value: 3
enum16 | IntvTyp |  |  | Name: WEEKDAY; Value: 4
enum16 | IntvTyp |  |  | Name: HOLIDAY; Value: 5
enum16 | IntvTyp |  |  | Name: WEEKEND; Value: 6
enum16 | IntvTyp |  |  | Name: YEARLY; Value: 7
enum16 | XTyp |  |  | Name: UNSET; Value: 0
enum16 | XTyp |  |  | Name: TIME; Value: 1
enum16 | XTyp |  |  | Name: TEMP; Value: 2
enum16 | XTyp |  |  | Name: PRICE; Value: 3
enum16 | XTyp |  |  | Name: OTHER; Value: 99
enum16 | YTyp |  |  | Name: UNSET; Value: 0
enum16 | YTyp |  |  | Name: WMax; Value: 1
enum16 | YTyp |  |  | Name: RSRVD2; Value: 2
enum16 | YTyp |  |  | Name: PF; Value: 3
enum16 | YTyp |  |  | Name: RSRVD4; Value: 4
enum16 | YTyp |  |  | Name: WATT_PRICE; Value: 5
enum16 | YTyp |  |  | Name: VAR_PRICE; Value: 6
enum16 | YTyp |  |  | Name: RSRVD7; Value: 7
enum16 | YTyp |  |  | Name: VOLT_VAR_ARRAY; Value: 8
enum16 | YTyp |  |  | Name: WChaGra; Value: 9
enum16 | YTyp |  |  | Name: WDisChaGra; Value: 10
enum16 | YTyp |  |  | Name: VArAval; Value: 11
enum16 | YTyp |  |  | Name: Schedule; Value: 12
enum16 | YTyp |  |  | Name: OTHER; Value: 99

## 134
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Freq-Watt Crv | 134 | uint16 |  |  | R | M | Curve-Based Frequency-Watt | Ref 3: 8.9.1.2, 8.9.4.2
Header |  | 1 |  | 1 | L |  | 10 + (RB Count * 58) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | ActCrv | ActCrv |  | uint16 |  |  | RW | M | Index of active curve. 0=no active curve.
Fixed Block |  | 3 | 1 | 1 | ModEna | ModEna |  | bitfield16 |  |  | RW | M | Is curve-based Frequency-Watt control active.
Fixed Block |  | 4 | 2 | 1 | WinTms | WinTms |  | uint16 | Secs |  | RW | O | Time window for freq-watt change.
Fixed Block |  | 5 | 3 | 1 | RvrtTms | RvrtTms |  | uint16 | Secs |  | RW | O | Timeout period for freq-watt curve selection.
Fixed Block |  | 6 | 4 | 1 | RmpTms | RmpTms |  | uint16 | Secs |  | RW | O | Ramp time for moving from current mode to new mode.
Fixed Block |  | 7 | 5 | 1 | NCrv | NCrv |  | uint16 |  |  | R | M | Number of curves supported (recommend min. 4).
Fixed Block |  | 8 | 6 | 1 | NPt | NPt |  | uint16 |  |  | R | M | Number of curve points supported (maximum of 10).
Fixed Block |  | 9 | 7 | 1 | Hz_SF | Hz_SF |  | sunssf | SF |  | R | M | Scale factor for frequency.
Fixed Block |  | 10 | 8 | 1 | W_SF | W_SF |  | sunssf | SF |  | R | M | Scale factor for percent WRef.
Fixed Block |  | 11 | 9 | 1 | RmpIncDec_SF | RmpIncDec_SF |  | sunssf | SF |  | R | O | Scale factor for increment and decrement ramps.
Repeating Block |  | 12 | 0 | 1 | ActPt | ActPt |  | uint16 |  |  | RW | M | Number of active points in array.
Repeating Block |  | 13 | 1 | 1 | Hz1 | Hz1 |  | uint16 | Hz | Hz_SF | RW | M | Point 1 Hertz.
Repeating Block |  | 14 | 2 | 1 | W1 | W1 |  | int16 | % WRef | W_SF | RW | M | Point 1 Watts.
Repeating Block |  | 15 | 3 | 1 | Hz2 | Hz2 |  | uint16 | Hz | Hz_SF | RW | O | Point 2 Hertz.
Repeating Block |  | 16 | 4 | 1 | W2 | W2 |  | int16 | % WRef | W_SF | RW | O | Point 2 Watts.
Repeating Block |  | 17 | 5 | 1 | Hz3 | Hz3 |  | uint16 | Hz | Hz_SF | RW | O | Point 3 Hertz.
Repeating Block |  | 18 | 6 | 1 | W3 | W3 |  | int16 | % WRef | W_SF | RW | O | Point 3 Watts.
Repeating Block |  | 19 | 7 | 1 | Hz4 | Hz4 |  | uint16 | Hz | Hz_SF | RW | O | Point 4 Hertz.
Repeating Block |  | 20 | 8 | 1 | W4 | W4 |  | int16 | % WRef | W_SF | RW | O | Point 4 Watts.
Repeating Block |  | 21 | 9 | 1 | Hz5 | Hz5 |  | uint16 | Hz | Hz_SF | RW | O | Point 5 Hertz.
Repeating Block |  | 22 | 10 | 1 | W5 | W5 |  | int16 | % WRef | W_SF | RW | O | Point 5 Watts.
Repeating Block |  | 23 | 11 | 1 | Hz6 | Hz6 |  | uint16 | Hz | Hz_SF | RW | O | Point 6 Hertz.
Repeating Block |  | 24 | 12 | 1 | W6 | W6 |  | int16 | % WRef | W_SF | RW | O | Point 6 Watts.
Repeating Block |  | 25 | 13 | 1 | Hz7 | Hz7 |  | uint16 | Hz | Hz_SF | RW | O | Point 7 Hertz.
Repeating Block |  | 26 | 14 | 1 | W7 | W7 |  | int16 | % WRef | W_SF | RW | O | Point 7 Watts.
Repeating Block |  | 27 | 15 | 1 | Hz8 | Hz8 |  | uint16 | Hz | Hz_SF | RW | O | Point 8 Hertz.
Repeating Block |  | 28 | 16 | 1 | W8 | W8 |  | int16 | % WRef | W_SF | RW | O | Point 8 Watts.
Repeating Block |  | 29 | 17 | 1 | Hz9 | Hz9 |  | uint16 | Hz | Hz_SF | RW | O | Point 9 Hertz.
Repeating Block |  | 30 | 18 | 1 | W9 | W9 |  | int16 | % WRef | W_SF | RW | O | Point 9 Watts.
Repeating Block |  | 31 | 19 | 1 | Hz10 | Hz10 |  | uint16 | Hz | Hz_SF | RW | O | Point 10 Hertz.
Repeating Block |  | 32 | 20 | 1 | W10 | W10 |  | int16 | % WRef | W_SF | RW | O | Point 10 Watts.
Repeating Block |  | 33 | 21 | 1 | Hz11 | Hz11 |  | uint16 | Hz | Hz_SF | RW | O | Point 11 Hertz.
Repeating Block |  | 34 | 22 | 1 | W11 | W11 |  | int16 | % WRef | W_SF | RW | O | Point 11 Watts.
Repeating Block |  | 35 | 23 | 1 | Hz12 | Hz12 |  | uint16 | Hz | Hz_SF | RW | O | Point 12 Hertz.
Repeating Block |  | 36 | 24 | 1 | W12 | W12 |  | int16 | % WRef | W_SF | RW | O | Point 12 Watts.
Repeating Block |  | 37 | 25 | 1 | Hz13 | Hz13 |  | uint16 | Hz | Hz_SF | RW | O | Point 13 Hertz.
Repeating Block |  | 38 | 26 | 1 | W13 | W13 |  | int16 | % WRef | W_SF | RW | O | Point 13 Watts.
Repeating Block |  | 39 | 27 | 1 | Hz14 | Hz14 |  | uint16 | Hz | Hz_SF | RW | O | Point 14 Hertz.
Repeating Block |  | 40 | 28 | 1 | W14 | W14 |  | int16 | % WRef | W_SF | RW | O | Point 14 Watts.
Repeating Block |  | 41 | 29 | 1 | Hz15 | Hz15 |  | uint16 | Hz | Hz_SF | RW | O | Point 15 Hertz.
Repeating Block |  | 42 | 30 | 1 | W15 | W15 |  | int16 | % WRef | W_SF | RW | O | Point 15 Watts.
Repeating Block |  | 43 | 31 | 1 | Hz16 | Hz16 |  | uint16 | Hz | Hz_SF | RW | O | Point 16 Hertz.
Repeating Block |  | 44 | 32 | 1 | W16 | W16 |  | int16 | % WRef | W_SF | RW | O | Point 16 Watts.
Repeating Block |  | 45 | 33 | 1 | Hz17 | Hz17 |  | uint16 | Hz | Hz_SF | RW | O | Point 17 Hertz.
Repeating Block |  | 46 | 34 | 1 | W17 | W17 |  | int16 | % WRef | W_SF | RW | O | Point 17 Watts.
Repeating Block |  | 47 | 35 | 1 | Hz18 | Hz18 |  | uint16 | Hz | Hz_SF | RW | O | Point 18 Hertz.
Repeating Block |  | 48 | 36 | 1 | W18 | W18 |  | int16 | % WRef | W_SF | RW | O | Point 18 Watts.
Repeating Block |  | 49 | 37 | 1 | Hz19 | Hz19 |  | uint16 | Hz | Hz_SF | RW | O | Point 19 Hertz.
Repeating Block |  | 50 | 38 | 1 | W19 | W19 |  | int16 | % WRef | W_SF | RW | O | Point 19 Watts.
Repeating Block |  | 51 | 39 | 1 | Hz20 | Hz20 |  | uint16 | Hz | Hz_SF | RW | O | Point 20 Hertz.
Repeating Block |  | 52 | 40 | 1 | W20 | W20 |  | int16 | % WRef | W_SF | RW | O | Point 20 Watts.
Repeating Block |  | 53 | 41 | 8 | CrvNam | CrvNam |  | string |  |  | RW | O | Optional description for curve. (Max 16 chars)
Repeating Block |  | 61 | 49 | 1 | RmpPT1Tms | RmpPT1Tms |  | uint16 | Secs |  | RW | O | The time of the PT1 in seconds (time to accomplish a change of 95%).
Repeating Block |  | 62 | 50 | 1 | RmpDecTmm | RmpDecTmm |  | uint16 | % WMax/min | RmpIncDec_SF | RW | O | The maximum rate at which the power value may be reduced in response to changes in the frequency value.
Repeating Block |  | 63 | 51 | 1 | RmpIncTmm | RmpIncTmm |  | uint16 | % WMax/min | RmpIncDec_SF | RW | O | The maximum rate at which the power value may be increased in response to changes in the frequency value.
Repeating Block |  | 64 | 52 | 1 | RmpRsUp | RmpRsUp |  | uint16 | % WMax/min | RmpIncDec_SF | RW | O | The maximum rate at which the power may be increased after releasing the frozen value of snap shot function.
Repeating Block |  | 65 | 53 | 1 | SnptW | SnptW |  | bitfield16 |  |  | RW | M | 1=enable snapshot/capture mode
Repeating Block |  | 66 | 54 | 1 | WRef | WRef |  | uint16 | W | W_SF | RW | O | Reference active power (default = WMax).
Repeating Block |  | 67 | 55 | 1 | WRefStrHz | WRefStrHz |  | uint16 | Hz | Hz_SF | RW | O | Frequency deviation from nominal frequency at the time of the snapshot to start constraining power output.
Repeating Block |  | 68 | 56 | 1 | WRefStopHz | WRefStopHz |  | uint16 | Hz | Hz_SF | RW | O | Frequency deviation from nominal frequency at which to release the power output.
Repeating Block |  | 69 | 57 | 1 | ReadOnly | ReadOnly |  | enum16 |  |  | R | M | Enumerated value indicates if curve is read-only or can be modified.
bitfield16 | ModEna |  |  | Name: ENABLED; Value: 0
enum16 | ReadOnly |  |  | Name: READWRITE; Value: 0
enum16 | ReadOnly |  |  | Name: READONLY; Value: 1

## 135
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | LFRT | 135 | uint16 |  |  | R | M | Low Frequency Ride-through | Ref 4: 11
Header |  | 1 |  | 1 | L |  | 10 + (RB Count * 50) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | ActCrv | ActCrv |  | uint16 |  |  | RW | M | Index of active curve. 0=no active curve.
Fixed Block |  | 3 | 1 | 1 | ModEna | ModEna |  | bitfield16 |  |  | RW | M | LHzRT control mode. Enable active curve. Bitfield value.
Fixed Block |  | 4 | 2 | 1 | WinTms | WinTms |  | uint16 | Secs |  | RW | O | Time window for LFRT change. | Setting is ignored for LFRT controls.
Fixed Block |  | 5 | 3 | 1 | RvrtTms | RvrtTms |  | uint16 | Secs |  | RW | O | Timeout period for LFRT curve selection. | Setting is ignored for LFRT controls.
Fixed Block |  | 6 | 4 | 1 | RmpTms | RmpTms |  | uint16 | Secs |  | RW | O | Ramp time for moving from current mode to new mode. | Setting is ignored for LFRT controls.
Fixed Block |  | 7 | 5 | 1 | NCrv | NCrv |  | uint16 |  |  | R | M | Number of curves supported (recommend 4).
Fixed Block |  | 8 | 6 | 1 | NPt | NPt |  | uint16 |  |  | R | M | Number of curve points supported (maximumn of 20).
Fixed Block |  | 9 | 7 | 1 | Tms_SF | Tms_SF |  | sunssf |  |  | R | M | Scale factor for duration.
Fixed Block |  | 10 | 8 | 1 | Hz_SF | Hz_SF |  | sunssf |  |  | R | M | Scale factor for frequency.
Fixed Block |  | 11 | 9 | Size: 1; Name: Pad; Type: pad; R/W: R | O
Repeating Block |  | 12 | 0 | 1 | ActPt | ActPt |  | uint16 |  |  | RW | M | Number of active points in array.
Repeating Block |  | 13 | 1 | 1 | Tms1 | Tms1 |  | uint16 | Secs | Tms_SF | RW | M | Point 1 must disconnect duration.
Repeating Block |  | 14 | 2 | 1 | Hz1 | Hz1 |  | uint16 | Hz | Hz_SF | RW | M | Point 1 must disconnect frequency.
Repeating Block |  | 15 | 3 | 1 | Tms2 | Tms2 |  | uint16 | Secs | Tms_SF | RW | O | Point 2 must disconnect duration.
Repeating Block |  | 16 | 4 | 1 | Hz2 | Hz2 |  | uint16 | Hz | Hz_SF | RW | O | Point 2 must disconnect frequency.
Repeating Block |  | 17 | 5 | 1 | Tms3 | Tms3 |  | uint16 | Secs | Tms_SF | RW | O | Point 3 must disconnect duration.
Repeating Block |  | 18 | 6 | 1 | Hz3 | Hz3 |  | uint16 | Hz | Hz_SF | RW | O | Point 3 must disconnect frequency.
Repeating Block |  | 19 | 7 | 1 | Tms4 | Tms4 |  | uint16 | Secs | Tms_SF | RW | O | Point 4 must disconnect duration.
Repeating Block |  | 20 | 8 | 1 | Hz4 | Hz4 |  | uint16 | Hz | Hz_SF | RW | O | Point 4 must disconnect frequency.
Repeating Block |  | 21 | 9 | 1 | Tms5 | Tms5 |  | uint16 | Secs | Tms_SF | RW | O | Point 5 must disconnect duration.
Repeating Block |  | 22 | 10 | 1 | Hz5 | Hz5 |  | uint16 | Hz | Hz_SF | RW | O | Point 5 must disconnect frequency.
Repeating Block |  | 23 | 11 | 1 | Tms6 | Tms6 |  | uint16 | Secs | Tms_SF | RW | O | Point 6 must disconnect duration.
Repeating Block |  | 24 | 12 | 1 | Hz6 | Hz6 |  | uint16 | Hz | Hz_SF | RW | O | Point 6 must disconnect frequency.
Repeating Block |  | 25 | 13 | 1 | Tms7 | Tms7 |  | uint16 | Secs | Tms_SF | RW | O | Point 7 must disconnect duration.
Repeating Block |  | 26 | 14 | 1 | Hz7 | Hz7 |  | uint16 | Hz | Hz_SF | RW | O | Point 7 must disconnect frequency.
Repeating Block |  | 27 | 15 | 1 | Tms8 | Tms8 |  | uint16 | Secs | Tms_SF | RW | O | Point 8 must disconnect duration.
Repeating Block |  | 28 | 16 | 1 | Hz8 | Hz8 |  | uint16 | Hz | Hz_SF | RW | O | Point 8 must disconnect frequency.
Repeating Block |  | 29 | 17 | 1 | Tms9 | Tms9 |  | uint16 | Secs | Tms_SF | RW | O | Point 9 must disconnect duration.
Repeating Block |  | 30 | 18 | 1 | Hz9 | Hz9 |  | uint16 | Hz | Hz_SF | RW | O | Point 9 must disconnect frequency.
Repeating Block |  | 31 | 19 | 1 | Tms10 | Tms10 |  | uint16 | Secs | Tms_SF | RW | O | Point 10 must disconnect duration.
Repeating Block |  | 32 | 20 | 1 | Hz10 | Hz10 |  | uint16 | Hz | Hz_SF | RW | O | Point 10 must disconnect frequency.
Repeating Block |  | 33 | 21 | 1 | Tms11 | Tms11 |  | uint16 | Secs | Tms_SF | RW | O | Point 11 must disconnect duration.
Repeating Block |  | 34 | 22 | 1 | Hz11 | Hz11 |  | uint16 | Hz | Hz_SF | RW | O | Point 11 must disconnect frequency.
Repeating Block |  | 35 | 23 | 1 | Tms12 | Tms12 |  | uint16 | Secs | Tms_SF | RW | O | Point 12 must disconnect duration.
Repeating Block |  | 36 | 24 | 1 | Hz12 | Hz12 |  | uint16 | Hz | Hz_SF | RW | O | Point 12 must disconnect frequency.
Repeating Block |  | 37 | 25 | 1 | Tms13 | Tms13 |  | uint16 | Secs | Tms_SF | RW | O | Point 13 must disconnect duration.
Repeating Block |  | 38 | 26 | 1 | Hz13 | Hz13 |  | uint16 | Hz | Hz_SF | RW | O | Point 13 must disconnect frequency.
Repeating Block |  | 39 | 27 | 1 | Tms14 | Tms14 |  | uint16 | Secs | Tms_SF | RW | O | Point 14 must disconnect duration.
Repeating Block |  | 40 | 28 | 1 | Hz14 | Hz14 |  | uint16 | Hz | Hz_SF | RW | O | Point 14 must disconnect frequency.
Repeating Block |  | 41 | 29 | 1 | Tms15 | Tms15 |  | uint16 | Secs | Tms_SF | RW | O | Point 15 must disconnect duration.
Repeating Block |  | 42 | 30 | 1 | Hz15 | Hz15 |  | uint16 | Hz | Hz_SF | RW | O | Point 15 must disconnect frequency.
Repeating Block |  | 43 | 31 | 1 | Tms16 | Tms16 |  | uint16 | Secs | Tms_SF | RW | O | Point 16 must disconnect duration.
Repeating Block |  | 44 | 32 | 1 | Hz16 | Hz16 |  | uint16 | Hz | Hz_SF | RW | O | Point 16 must disconnect frequency.
Repeating Block |  | 45 | 33 | 1 | Tms17 | Tms17 |  | uint16 | Secs | Tms_SF | RW | O | Point 17 must disconnect duration.
Repeating Block |  | 46 | 34 | 1 | Hz17 | Hz17 |  | uint16 | Hz | Hz_SF | RW | O | Point 17 must disconnect frequency.
Repeating Block |  | 47 | 35 | 1 | Tms18 | Tms18 |  | uint16 | Secs | Tms_SF | RW | O | Point 18 must disconnect duration.
Repeating Block |  | 48 | 36 | 1 | Hz18 | Hz18 |  | uint16 | Hz | Hz_SF | RW | O | Point 18 must disconnect frequency.
Repeating Block |  | 49 | 37 | 1 | Tms19 | Tms19 |  | uint16 | Secs | Tms_SF | RW | O | Point 19 must disconnect duration.
Repeating Block |  | 50 | 38 | 1 | Hz19 | Hz19 |  | uint16 | Hz | Hz_SF | RW | O | Point 19 must disconnect frequency.
Repeating Block |  | 51 | 39 | 1 | Tms20 | Tms20 |  | uint16 | Secs | Tms_SF | RW | O | Point 20 must disconnect duration.
Repeating Block |  | 52 | 40 | 1 | Hz20 | Hz20 |  | uint16 | Hz | Hz_SF | RW | O | Point 20 must disconnect frequency.
Repeating Block |  | 53 | 41 | 8 | CrvNam | CrvNam |  | string |  |  | RW | O | Optional description for curve.
Repeating Block |  | 61 | 49 | 1 | ReadOnly | ReadOnly |  | enum16 |  |  | R | M | Enumerated value indicates if curve is read-only or can be modified.
bitfield16 | ModEna |  |  | Name: ENABLED; Value: 0
enum16 | ReadOnly |  |  | Name: READWRITE; Value: 0
enum16 | ReadOnly |  |  | Name: READONLY; Value: 1

## 136
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | HFRT | 136 | uint16 |  |  | R | M | High Frequency Ride-through | Ref 4: 11
Header |  | 1 |  | 1 | L |  | 10 + (RB Count * 50) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | ActCrv | ActCrv |  | uint16 |  |  | RW | M | Index of active curve. 0=no active curve.
Fixed Block |  | 3 | 1 | 1 | ModEna | ModEna |  | bitfield16 |  |  | RW | M | HFRT control mode. Enable active curve. Bitfield value.
Fixed Block |  | 4 | 2 | 1 | WinTms | WinTms |  | uint16 | Secs |  | RW | O | Time window for HFRT change. | Setting is ignored for HFRT controls.
Fixed Block |  | 5 | 3 | 1 | RvrtTms | RvrtTms |  | uint16 | Secs |  | RW | O | Timeout period for HFRT curve selection. | Setting is ignored for HFRT controls.
Fixed Block |  | 6 | 4 | 1 | RmpTms | RmpTms |  | uint16 | Secs |  | RW | O | Ramp time for moving from current mode to new mode. | Setting is ignored for HFRT controls.
Fixed Block |  | 7 | 5 | 1 | NCrv | NCrv |  | uint16 |  |  | R | M | Number of curves supported (recommend 4).
Fixed Block |  | 8 | 6 | 1 | NPt | NPt |  | uint16 |  |  | R | M | Number of curve points supported (maximumn of 20).
Fixed Block |  | 9 | 7 | 1 | Tms_SF | Tms_SF |  | sunssf |  |  | R | M | Scale factor for duration.
Fixed Block |  | 10 | 8 | 1 | Hz_SF | Hz_SF |  | sunssf |  |  | R | M | Scale factor for frequency.
Fixed Block |  | 11 | 9 | Size: 1; Name: Pad; Type: pad; R/W: R | O
Repeating Block |  | 12 | 0 | 1 | ActPt | ActPt |  | uint16 |  |  | RW | M | Number of active points in array.
Repeating Block |  | 13 | 1 | 1 | Tms1 | Tms1 |  | uint16 | Secs | Tms_SF | RW | M | Point 1 must disconnect duration.
Repeating Block |  | 14 | 2 | 1 | Hz1 | Hz1 |  | uint16 | Hz | Hz_SF | RW | M | Point 1 must disconnect frequency.
Repeating Block |  | 15 | 3 | 1 | Tms2 | Tms2 |  | uint16 | Secs | Tms_SF | RW | O | Point 2 must disconnect duration.
Repeating Block |  | 16 | 4 | 1 | Hz2 | Hz2 |  | uint16 | Hz | Hz_SF | RW | O | Point 2 must disconnect frequency.
Repeating Block |  | 17 | 5 | 1 | Tms3 | Tms3 |  | uint16 | Secs | Tms_SF | RW | O | Point 3 must disconnect duration.
Repeating Block |  | 18 | 6 | 1 | Hz3 | Hz3 |  | uint16 | Hz | Hz_SF | RW | O | Point 3 must disconnect frequency.
Repeating Block |  | 19 | 7 | 1 | Tms4 | Tms4 |  | uint16 | Secs | Tms_SF | RW | O | Point 4 must disconnect duration.
Repeating Block |  | 20 | 8 | 1 | Hz4 | Hz4 |  | uint16 | Hz | Hz_SF | RW | O | Point 4 must disconnect frequency.
Repeating Block |  | 21 | 9 | 1 | Tms5 | Tms5 |  | uint16 | Secs | Tms_SF | RW | O | Point 5 must disconnect duration.
Repeating Block |  | 22 | 10 | 1 | Hz5 | Hz5 |  | uint16 | Hz | Hz_SF | RW | O | Point 5 must disconnect frequency.
Repeating Block |  | 23 | 11 | 1 | Tms6 | Tms6 |  | uint16 | Secs | Tms_SF | RW | O | Point 6 must disconnect duration.
Repeating Block |  | 24 | 12 | 1 | Hz6 | Hz6 |  | uint16 | Hz | Hz_SF | RW | O | Point 6 must disconnect frequency.
Repeating Block |  | 25 | 13 | 1 | Tms7 | Tms7 |  | uint16 | Secs | Tms_SF | RW | O | Point 7 must disconnect duration.
Repeating Block |  | 26 | 14 | 1 | Hz7 | Hz7 |  | uint16 | Hz | Hz_SF | RW | O | Point 7 must disconnect frequency.
Repeating Block |  | 27 | 15 | 1 | Tms8 | Tms8 |  | uint16 | Secs | Tms_SF | RW | O | Point 8 must disconnect duration.
Repeating Block |  | 28 | 16 | 1 | Hz8 | Hz8 |  | uint16 | Hz | Hz_SF | RW | O | Point 8 must disconnect frequency.
Repeating Block |  | 29 | 17 | 1 | Tms9 | Tms9 |  | uint16 | Secs | Tms_SF | RW | O | Point 9 must disconnect duration.
Repeating Block |  | 30 | 18 | 1 | Hz9 | Hz9 |  | uint16 | Hz | Hz_SF | RW | O | Point 9 must disconnect frequency.
Repeating Block |  | 31 | 19 | 1 | Tms10 | Tms10 |  | uint16 | Secs | Tms_SF | RW | O | Point 10 must disconnect duration.
Repeating Block |  | 32 | 20 | 1 | Hz10 | Hz10 |  | uint16 | Hz | Hz_SF | RW | O | Point 10 must disconnect frequency.
Repeating Block |  | 33 | 21 | 1 | Tms11 | Tms11 |  | uint16 | Secs | Tms_SF | RW | O | Point 11 must disconnect duration.
Repeating Block |  | 34 | 22 | 1 | Hz11 | Hz11 |  | uint16 | Hz | Hz_SF | RW | O | Point 11 must disconnect frequency.
Repeating Block |  | 35 | 23 | 1 | Tms12 | Tms12 |  | uint16 | Secs | Tms_SF | RW | O | Point 12 must disconnect duration.
Repeating Block |  | 36 | 24 | 1 | Hz12 | Hz12 |  | uint16 | Hz | Hz_SF | RW | O | Point 12 must disconnect frequency.
Repeating Block |  | 37 | 25 | 1 | Tms13 | Tms13 |  | uint16 | Secs | Tms_SF | RW | O | Point 13 must disconnect duration.
Repeating Block |  | 38 | 26 | 1 | Hz13 | Hz13 |  | uint16 | Hz | Hz_SF | RW | O | Point 13 must disconnect frequency.
Repeating Block |  | 39 | 27 | 1 | Tms14 | Tms14 |  | uint16 | Secs | Tms_SF | RW | O | Point 14 must disconnect duration.
Repeating Block |  | 40 | 28 | 1 | Hz14 | Hz14 |  | uint16 | Hz | Hz_SF | RW | O | Point 14 must disconnect frequency.
Repeating Block |  | 41 | 29 | 1 | Tms15 | Tms15 |  | uint16 | Secs | Tms_SF | RW | O | Point 15 must disconnect duration.
Repeating Block |  | 42 | 30 | 1 | Hz15 | Hz15 |  | uint16 | Hz | Hz_SF | RW | O | Point 15 must disconnect frequency.
Repeating Block |  | 43 | 31 | 1 | Tms16 | Tms16 |  | uint16 | Secs | Tms_SF | RW | O | Point 16 must disconnect duration.
Repeating Block |  | 44 | 32 | 1 | Hz16 | Hz16 |  | uint16 | Hz | Hz_SF | RW | O | Point 16 must disconnect frequency.
Repeating Block |  | 45 | 33 | 1 | Tms17 | Tms17 |  | uint16 | Secs | Tms_SF | RW | O | Point 17 must disconnect duration.
Repeating Block |  | 46 | 34 | 1 | Hz17 | Hz17 |  | uint16 | Hz | Hz_SF | RW | O | Point 17 must disconnect frequency.
Repeating Block |  | 47 | 35 | 1 | Tms18 | Tms18 |  | uint16 | Secs | Tms_SF | RW | O | Point 18 must disconnect duration.
Repeating Block |  | 48 | 36 | 1 | Hz18 | Hz18 |  | uint16 | Hz | Hz_SF | RW | O | Point 18 must disconnect frequency.
Repeating Block |  | 49 | 37 | 1 | Tms19 | Tms19 |  | uint16 | Secs | Tms_SF | RW | O | Point 19 must disconnect duration.
Repeating Block |  | 50 | 38 | 1 | Hz19 | Hz19 |  | uint16 | Hz | Hz_SF | RW | O | Point 19 must disconnect frequency.
Repeating Block |  | 51 | 39 | 1 | Tms20 | Tms20 |  | uint16 | Secs | Tms_SF | RW | O | Point 20 must disconnect duration.
Repeating Block |  | 52 | 40 | 1 | Hz20 | Hz20 |  | uint16 | Hz | Hz_SF | RW | O | Point 20 must disconnect frequency.
Repeating Block |  | 53 | 41 | 8 | CrvNam | CrvNam |  | string |  |  | RW | O | Optional description for curve.
Repeating Block |  | 61 | 49 | 1 | ReadOnly | ReadOnly |  | enum16 |  |  | R | M | Enumerated value indicates if curve is read-only or can be modified.
bitfield16 | ModEna |  |  | Name: ENABLED; Value: 0
enum16 | ReadOnly |  |  | Name: READWRITE; Value: 0
enum16 | ReadOnly |  |  | Name: READONLY; Value: 1

## 137
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | LVRTC | 137 | uint16 |  |  | R | M | LVRT must remain connected | Ref 4: 11
Header |  | 1 |  | 1 | L |  | 10 + (RB Count * 50) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | ActCrv | ActCrv |  | uint16 |  |  | RW | M | Index of active curve. 0=no active curve.
Fixed Block |  | 3 | 1 | 1 | ModEna | ModEna |  | bitfield16 |  |  | RW | M | LVRT control mode. Enable active curve. Bitfield value.
Fixed Block |  | 4 | 2 | 1 | WinTms | WinTms |  | uint16 | Secs |  | RW | O | Time window for LVRT change. | Setting is ignored for LVRT controls.
Fixed Block |  | 5 | 3 | 1 | RvrtTms | RvrtTms |  | uint16 | Secs |  | RW | O | Timeout period for LVRT curve selection. | Setting is ignored for LVRT controls.
Fixed Block |  | 6 | 4 | 1 | RmpTms | RmpTms |  | uint16 | Secs |  | RW | O | Ramp time for moving from current mode to new mode. | Setting is ignored for LVRT controls.
Fixed Block |  | 7 | 5 | 1 | NCrv | NCrv |  | uint16 |  |  | R | M | Number of curves supported (recommend 4).
Fixed Block |  | 8 | 6 | 1 | NPt | NPt |  | uint16 |  |  | R | M | Number of curve points supported (maximumn of 20).
Fixed Block |  | 9 | 7 | 1 | Tms_SF | Tms_SF |  | sunssf |  |  | R | M | Scale factor for duration.
Fixed Block |  | 10 | 8 | 1 | V_SF | V_SF |  | sunssf |  |  | R | M | Scale factor for percent VRef.
Fixed Block |  | 11 | 9 | Size: 1; Name: Pad; Type: pad; R/W: R | O
Repeating Block |  | 12 | 0 | 1 | ActPt | ActPt |  | uint16 |  |  | RW | M | Number of active points in array.
Repeating Block |  | 13 | 1 | 1 | Tms1 | Tms1 |  | uint16 | Secs | Tms_SF | RW | M | Point 1 must remain connected duration.
Repeating Block |  | 14 | 2 | 1 | V1 | V1 |  | uint16 | % VRef | V_SF | RW | M | Point 1 must remain connected voltage.
Repeating Block |  | 15 | 3 | 1 | Tms2 | Tms2 |  | uint16 | Secs | Tms_SF | RW | O | Point 2 must remain connected duration.
Repeating Block |  | 16 | 4 | 1 | V2 | V2 |  | uint16 | % VRef | V_SF | RW | O | Point 2 must remain connected voltage.
Repeating Block |  | 17 | 5 | 1 | Tms3 | Tms3 |  | uint16 | Secs | Tms_SF | RW | O | Point 3 must remain connected duration.
Repeating Block |  | 18 | 6 | 1 | V3 | V3 |  | uint16 | % VRef | V_SF | RW | O | Point 3 must remain connected voltage.
Repeating Block |  | 19 | 7 | 1 | Tms4 | Tms4 |  | uint16 | Secs | Tms_SF | RW | O | Point 4 must remain connected duration.
Repeating Block |  | 20 | 8 | 1 | V4 | V4 |  | uint16 | % VRef | V_SF | RW | O | Point 4 must remain connected voltage.
Repeating Block |  | 21 | 9 | 1 | Tms5 | Tms5 |  | uint16 | Secs | Tms_SF | RW | O | Point 5 must remain connected duration.
Repeating Block |  | 22 | 10 | 1 | V5 | V5 |  | uint16 | % VRef | V_SF | RW | O | Point 5 must remain connected voltage.
Repeating Block |  | 23 | 11 | 1 | Tms6 | Tms6 |  | uint16 | Secs | Tms_SF | RW | O | Point 6 must remain connected duration.
Repeating Block |  | 24 | 12 | 1 | V6 | V6 |  | uint16 | % VRef | V_SF | RW | O | Point 6 must remain connected voltage.
Repeating Block |  | 25 | 13 | 1 | Tms7 | Tms7 |  | uint16 | Secs | Tms_SF | RW | O | Point 7 must remain connected duration.
Repeating Block |  | 26 | 14 | 1 | V7 | V7 |  | uint16 | % VRef | V_SF | RW | O | Point 7 must remain connected voltage.
Repeating Block |  | 27 | 15 | 1 | Tms8 | Tms8 |  | uint16 | Secs | Tms_SF | RW | O | Point 8 must remain connected duration.
Repeating Block |  | 28 | 16 | 1 | V8 | V8 |  | uint16 | % VRef | V_SF | RW | O | Point 8 must remain connected voltage.
Repeating Block |  | 29 | 17 | 1 | Tms9 | Tms9 |  | uint16 | Secs | Tms_SF | RW | O | Point 9 must remain connected duration.
Repeating Block |  | 30 | 18 | 1 | V9 | V9 |  | uint16 | % VRef | V_SF | RW | O | Point 9 must remain connected voltage.
Repeating Block |  | 31 | 19 | 1 | Tms10 | Tms10 |  | uint16 | Secs | Tms_SF | RW | O | Point 10 must remain connected duration.
Repeating Block |  | 32 | 20 | 1 | V10 | V10 |  | uint16 | % VRef | V_SF | RW | O | Point 10 must remain connected voltage.
Repeating Block |  | 33 | 21 | 1 | Tms11 | Tms11 |  | uint16 | Secs | Tms_SF | RW | O | Point 11 must remain connected duration.
Repeating Block |  | 34 | 22 | 1 | V11 | V11 |  | uint16 | % VRef | V_SF | RW | O | Point 11 must remain connected voltage.
Repeating Block |  | 35 | 23 | 1 | Tms12 | Tms12 |  | uint16 | Secs | Tms_SF | RW | O | Point 12 must remain connected duration.
Repeating Block |  | 36 | 24 | 1 | V12 | V12 |  | uint16 | % VRef | V_SF | RW | O | Point 12 must remain connected voltage.
Repeating Block |  | 37 | 25 | 1 | Tms13 | Tms13 |  | uint16 | Secs | Tms_SF | RW | O | Point 13 must remain connected duration.
Repeating Block |  | 38 | 26 | 1 | V13 | V13 |  | uint16 | % VRef | V_SF | RW | O | Point 13 must remain connected voltage.
Repeating Block |  | 39 | 27 | 1 | Tms14 | Tms14 |  | uint16 | Secs | Tms_SF | RW | O | Point 14 must remain connected duration.
Repeating Block |  | 40 | 28 | 1 | V14 | V14 |  | uint16 | % VRef | V_SF | RW | O | Point 14 must remain connected voltage.
Repeating Block |  | 41 | 29 | 1 | Tms15 | Tms15 |  | uint16 | Secs | Tms_SF | RW | O | Point 15 must remain connected duration.
Repeating Block |  | 42 | 30 | 1 | V15 | V15 |  | uint16 | % VRef | V_SF | RW | O | Point 15 must remain connected voltage.
Repeating Block |  | 43 | 31 | 1 | Tms16 | Tms16 |  | uint16 | Secs | Tms_SF | RW | O | Point 16 must remain connected duration.
Repeating Block |  | 44 | 32 | 1 | V16 | V16 |  | uint16 | % VRef | V_SF | RW | O | Point 16 must remain connected voltage.
Repeating Block |  | 45 | 33 | 1 | Tms17 | Tms17 |  | uint16 | Secs | Tms_SF | RW | O | Point 17 must remain connected duration.
Repeating Block |  | 46 | 34 | 1 | V17 | V17 |  | uint16 | % VRef | V_SF | RW | O | Point 17 must remain connected voltage.
Repeating Block |  | 47 | 35 | 1 | Tms18 | Tms18 |  | uint16 | Secs | Tms_SF | RW | O | Point 18 must remain connected duration.
Repeating Block |  | 48 | 36 | 1 | V18 | V18 |  | uint16 | % VRef | V_SF | RW | O | Point 18 must remain connected voltage.
Repeating Block |  | 49 | 37 | 1 | Tms19 | Tms19 |  | uint16 | Secs | Tms_SF | RW | O | Point 19 must remain connected duration.
Repeating Block |  | 50 | 38 | 1 | V19 | V19 |  | uint16 | % VRef | V_SF | RW | O | Point 19 must remain connected voltage.
Repeating Block |  | 51 | 39 | 1 | Tms20 | Tms20 |  | uint16 | Secs | Tms_SF | RW | O | Point 20 must remain connected duration.
Repeating Block |  | 52 | 40 | 1 | V20 | V20 |  | uint16 | % VRef | V_SF | RW | O | Point 20 must remain connected voltage.
Repeating Block |  | 53 | 41 | 8 | CrvNam | CrvNam |  | string |  |  | RW | O | Optional description for curve.
Repeating Block |  | 61 | 49 | 1 | ReadOnly | ReadOnly |  | enum16 |  |  | R | M | Enumerated value indicates if curve is read-only or can be modified.
bitfield16 | ModEna |  |  | Name: ENABLED; Value: 0
enum16 | ReadOnly |  |  | Name: READWRITE; Value: 0
enum16 | ReadOnly |  |  | Name: READONLY; Value: 1

## 138
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | HVRTC | 138 | uint16 |  |  | R | M | HVRT must remain connected | Ref 4: 11
Header |  | 1 |  | 1 | L |  | 10 + (RB Count * 50) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | ActCrv | ActCrv |  | uint16 |  |  | RW | M | Index of active curve. 0=no active curve.
Fixed Block |  | 3 | 1 | 1 | ModEna | ModEna |  | bitfield16 |  |  | RW | M | HVRT control mode. Enable active curve. Bitfield value.
Fixed Block |  | 4 | 2 | 1 | WinTms | WinTms |  | uint16 | Secs |  | RW | O | Time window for HVRT change. | Setting is ignored for HVRT controls.
Fixed Block |  | 5 | 3 | 1 | RvrtTms | RvrtTms |  | uint16 | Secs |  | RW | O | Timeout period for HVRT curve selection. | Setting is ignored for HVRT controls.
Fixed Block |  | 6 | 4 | 1 | RmpTms | RmpTms |  | uint16 | Secs |  | RW | O | Ramp time for moving from current mode to new mode. | Setting is ignored for HVRT controls.
Fixed Block |  | 7 | 5 | 1 | NCrv | NCrv |  | uint16 |  |  | R | M | Number of curves supported (recommend 4).
Fixed Block |  | 8 | 6 | 1 | NPt | NPt |  | uint16 |  |  | R | M | Number of curve points supported (maximumn of 20).
Fixed Block |  | 9 | 7 | 1 | Tms_SF | Tms_SF |  | sunssf |  |  | R | M | Scale factor for duration.
Fixed Block |  | 10 | 8 | 1 | V_SF | V_SF |  | sunssf |  |  | R | M | Scale factor for percent VRef.
Fixed Block |  | 11 | 9 | Size: 1; Name: Pad; Type: pad; R/W: R | O
Repeating Block |  | 12 | 0 | 1 | ActPt | ActPt |  | uint16 |  |  | RW | M | Number of active points in array.
Repeating Block |  | 13 | 1 | 1 | Tms1 | Tms1 |  | uint16 | Secs | Tms_SF | RW | M | Point 1 must remain connected duration.
Repeating Block |  | 14 | 2 | 1 | V1 | V1 |  | uint16 | % VRef | V_SF | RW | M | Point 1 must remain connected voltage.
Repeating Block |  | 15 | 3 | 1 | Tms2 | Tms2 |  | uint16 | Secs | Tms_SF | RW | O | Point 2 must remain connected duration.
Repeating Block |  | 16 | 4 | 1 | V2 | V2 |  | uint16 | % VRef | V_SF | RW | O | Point 2 must remain connected voltage.
Repeating Block |  | 17 | 5 | 1 | Tms3 | Tms3 |  | uint16 | Secs | Tms_SF | RW | O | Point 3 must remain connected duration.
Repeating Block |  | 18 | 6 | 1 | V3 | V3 |  | uint16 | % VRef | V_SF | RW | O | Point 3 must remain connected voltage.
Repeating Block |  | 19 | 7 | 1 | Tms4 | Tms4 |  | uint16 | Secs | Tms_SF | RW | O | Point 4 must remain connected duration.
Repeating Block |  | 20 | 8 | 1 | V4 | V4 |  | uint16 | % VRef | V_SF | RW | O | Point 4 must remain connected voltage.
Repeating Block |  | 21 | 9 | 1 | Tms5 | Tms5 |  | uint16 | Secs | Tms_SF | RW | O | Point 5 must remain connected duration.
Repeating Block |  | 22 | 10 | 1 | V5 | V5 |  | uint16 | % VRef | V_SF | RW | O | Point 5 must remain connected voltage.
Repeating Block |  | 23 | 11 | 1 | Tms6 | Tms6 |  | uint16 | Secs | Tms_SF | RW | O | Point 6 must remain connected duration.
Repeating Block |  | 24 | 12 | 1 | V6 | V6 |  | uint16 | % VRef | V_SF | RW | O | Point 6 must remain connected voltage.
Repeating Block |  | 25 | 13 | 1 | Tms7 | Tms7 |  | uint16 | Secs | Tms_SF | RW | O | Point 7 must remain connected duration.
Repeating Block |  | 26 | 14 | 1 | V7 | V7 |  | uint16 | % VRef | V_SF | RW | O | Point 7 must remain connected voltage.
Repeating Block |  | 27 | 15 | 1 | Tms8 | Tms8 |  | uint16 | Secs | Tms_SF | RW | O | Point 8 must remain connected duration.
Repeating Block |  | 28 | 16 | 1 | V8 | V8 |  | uint16 | % VRef | V_SF | RW | O | Point 8 must remain connected voltage.
Repeating Block |  | 29 | 17 | 1 | Tms9 | Tms9 |  | uint16 | Secs | Tms_SF | RW | O | Point 9 must remain connected duration.
Repeating Block |  | 30 | 18 | 1 | V9 | V9 |  | uint16 | % VRef | V_SF | RW | O | Point 9 must remain connected voltage.
Repeating Block |  | 31 | 19 | 1 | Tms10 | Tms10 |  | uint16 | Secs | Tms_SF | RW | O | Point 10 must remain connected duration.
Repeating Block |  | 32 | 20 | 1 | V10 | V10 |  | uint16 | % VRef | V_SF | RW | O | Point 10 must remain connected voltage.
Repeating Block |  | 33 | 21 | 1 | Tms11 | Tms11 |  | uint16 | Secs | Tms_SF | RW | O | Point 11 must remain connected duration.
Repeating Block |  | 34 | 22 | 1 | V11 | V11 |  | uint16 | % VRef | V_SF | RW | O | Point 11 must remain connected voltage.
Repeating Block |  | 35 | 23 | 1 | Tms12 | Tms12 |  | uint16 | Secs | Tms_SF | RW | O | Point 12 must remain connected duration.
Repeating Block |  | 36 | 24 | 1 | V12 | V12 |  | uint16 | % VRef | V_SF | RW | O | Point 12 must remain connected voltage.
Repeating Block |  | 37 | 25 | 1 | Tms13 | Tms13 |  | uint16 | Secs | Tms_SF | RW | O | Point 13 must remain connected duration.
Repeating Block |  | 38 | 26 | 1 | V13 | V13 |  | uint16 | % VRef | V_SF | RW | O | Point 13 must remain connected voltage.
Repeating Block |  | 39 | 27 | 1 | Tms14 | Tms14 |  | uint16 | Secs | Tms_SF | RW | O | Point 14 must remain connected duration.
Repeating Block |  | 40 | 28 | 1 | V14 | V14 |  | uint16 | % VRef | V_SF | RW | O | Point 14 must remain connected voltage.
Repeating Block |  | 41 | 29 | 1 | Tms15 | Tms15 |  | uint16 | Secs | Tms_SF | RW | O | Point 15 must remain connected duration.
Repeating Block |  | 42 | 30 | 1 | V15 | V15 |  | uint16 | % VRef | V_SF | RW | O | Point 15 must remain connected voltage.
Repeating Block |  | 43 | 31 | 1 | Tms16 | Tms16 |  | uint16 | Secs | Tms_SF | RW | O | Point 16 must remain connected duration.
Repeating Block |  | 44 | 32 | 1 | V16 | V16 |  | uint16 | % VRef | V_SF | RW | O | Point 16 must remain connected voltage.
Repeating Block |  | 45 | 33 | 1 | Tms17 | Tms17 |  | uint16 | Secs | Tms_SF | RW | O | Point 17 must remain connected duration.
Repeating Block |  | 46 | 34 | 1 | V17 | V17 |  | uint16 | % VRef | V_SF | RW | O | Point 17 must remain connected voltage.
Repeating Block |  | 47 | 35 | 1 | Tms18 | Tms18 |  | uint16 | Secs | Tms_SF | RW | O | Point 18 must remain connected duration.
Repeating Block |  | 48 | 36 | 1 | V18 | V18 |  | uint16 | % VRef | V_SF | RW | O | Point 18 must remain connected voltage.
Repeating Block |  | 49 | 37 | 1 | Tms19 | Tms19 |  | uint16 | Secs | Tms_SF | RW | O | Point 19 must remain connected duration.
Repeating Block |  | 50 | 38 | 1 | V19 | V19 |  | uint16 | % VRef | V_SF | RW | O | Point 19 must remain connected voltage.
Repeating Block |  | 51 | 39 | 1 | Tms20 | Tms20 |  | uint16 | Secs | Tms_SF | RW | O | Point 20 must remain connected duration.
Repeating Block |  | 52 | 40 | 1 | V20 | V20 |  | uint16 | % VRef | V_SF | RW | O | Point 20 must remain connected voltage.
Repeating Block |  | 53 | 41 | 8 | CrvNam | CrvNam |  | string |  |  | RW | O | Optional description for curve.
Repeating Block |  | 61 | 49 | 1 | ReadOnly | ReadOnly |  | enum16 |  |  | R | M | Enumerated value indicates if curve is read-only or can be modified.
bitfield16 | ModEna |  |  | Name: ENABLED; Value: 0
enum16 | ReadOnly |  |  | Name: READWRITE; Value: 0
enum16 | ReadOnly |  |  | Name: READONLY; Value: 1

## 160
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Multiple MPPT Inverter Extension Model | 160 | uint16 |  |  | R | M
Header |  | 1 |  | 1 | L |  | 8 + (RB Count * 20) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | DCA_SF | Current Scale Factor |  | sunssf |  |  | R | O
Fixed Block |  | 3 | 1 | 1 | DCV_SF | Voltage Scale Factor |  | sunssf |  |  | R | O
Fixed Block |  | 4 | 2 | 1 | DCW_SF | Power Scale Factor |  | sunssf |  |  | R | O
Fixed Block |  | 5 | 3 | 1 | DCWH_SF | Energy Scale Factor |  | sunssf |  |  | R | O
Fixed Block |  | 6 | 4 | 2 | Evt | Global Events |  | bitfield32 |  |  | R | O
Fixed Block |  | 8 | 6 | 1 | N | Number of Modules |  | count |  |  | R | O
Fixed Block |  | 9 | 7 | 1 | TmsPer | Timestamp Period |  | uint16 |  |  | R | O
Repeating Block |  | 10 | 0 | 1 | ID | Input ID |  | uint16 |  |  | R | O
Repeating Block |  | 11 | 1 | 8 | IDStr | Input ID Sting |  | string |  |  | R | O
Repeating Block |  | 19 | 9 | 1 | DCA | DC Current |  | uint16 | A | DCA_SF | R | O
Repeating Block |  | 20 | 10 | 1 | DCV | DC Voltage |  | uint16 | V | DCV_SF | R | O
Repeating Block |  | 21 | 11 | 1 | DCW | DC Power |  | uint16 | W | DCW_SF | R | O
Repeating Block |  | 22 | 12 | 2 | DCWH | Lifetime Energy |  | acc32 | Wh | DCWH_SF | R | O
Repeating Block |  | 24 | 14 | 2 | Tms | Timestamp |  | uint32 | Secs |  | R | O
Repeating Block |  | 26 | 16 | 1 | Tmp | Temperature |  | int16 | C |  | R | O
Repeating Block |  | 27 | 17 | 1 | DCSt | Operating State |  | enum16 |  |  | R | O
Repeating Block |  | 28 | 18 | 2 | DCEvt | Module Events |  | bitfield32 |  |  | R | O
bitfield32 | Evt |  |  | Name: GROUND_FAULT; Label: Ground Fault; Value: 0
bitfield32 | Evt |  |  | Name: INPUT_OVER_VOLTAGE; Label: Input Over Voltage; Value: 1
bitfield32 | Evt |  |  | Name: RESERVED; Label: Reserved; Value: 19
bitfield32 | Evt |  |  | Name: DC_DISCONNECT; Label: DC Disconnect; Value: 3
bitfield32 | Evt |  |  | Name: CABINET_OPEN; Label: Cabinet Open; Value: 5
bitfield32 | Evt |  |  | Name: MANUAL_SHUTDOWN; Label: Manual Shutdown; Value: 6
bitfield32 | Evt |  |  | Name: OVER_TEMP; Label: Over Temperature; Value: 7
bitfield32 | Evt |  |  | Name: BLOWN_FUSE; Label: Blown Fuse; Value: 12
bitfield32 | Evt |  |  | Name: UNDER_TEMP; Label: Under Temperature; Value: 13
bitfield32 | Evt |  |  | Name: MEMORY_LOSS; Label: Memory Loss; Value: 14
bitfield32 | Evt |  |  | Name: ARC_DETECTION; Label: Arc Detection; Value: 15
bitfield32 | Evt |  |  | Name: TEST_FAILED; Label: Test Failed; Value: 20
bitfield32 | Evt |  |  | Name: INPUT_UNDER_VOLTAGE; Label: Under Voltage; Value: 21
bitfield32 | Evt |  |  | Name: INPUT_OVER_CURRENT; Label: Over Current; Value: 22
enum16 | DCSt |  |  | Name: OFF; Label: Off; Value: 1
enum16 | DCSt |  |  | Name: SLEEPING; Label: Sleeping; Value: 2
enum16 | DCSt |  |  | Name: STARTING; Label: Starting; Value: 3
enum16 | DCSt |  |  | Name: MPPT; Label: MPPT; Value: 4
enum16 | DCSt |  |  | Name: THROTTLED; Label: Throttled; Value: 5
enum16 | DCSt |  |  | Name: SHUTTING_DOWN; Label: Shutting Down; Value: 6
enum16 | DCSt |  |  | Name: FAULT; Label: Fault; Value: 7
enum16 | DCSt |  |  | Name: STANDBY; Label: Standby; Value: 8
enum16 | DCSt |  |  | Name: TEST; Label: Test; Value: 9
enum16 | DCSt |  |  | Name: RESERVED; Label: Reserved; Value: 19
bitfield32 | DCEvt |  |  | Name: GROUND_FAULT; Label: Ground Fault; Value: 0
bitfield32 | DCEvt |  |  | Name: INPUT_OVER_VOLTAGE; Label: Input Over Voltage; Value: 1
bitfield32 | DCEvt |  |  | Name: RESERVED; Label: Reserved; Value: 19
bitfield32 | DCEvt |  |  | Name: DC_DISCONNECT; Label: DC Disconnect; Value: 3
bitfield32 | DCEvt |  |  | Name: CABINET_OPEN; Label: Cabinet Open; Value: 5
bitfield32 | DCEvt |  |  | Name: MANUAL_SHUTDOWN; Label: Manual Shutdown; Value: 6
bitfield32 | DCEvt |  |  | Name: OVER_TEMP; Label: Over Temperature; Value: 7
bitfield32 | DCEvt |  |  | Name: BLOWN_FUSE; Label: Blown Fuse; Value: 12
bitfield32 | DCEvt |  |  | Name: UNDER_TEMP; Label: Under Temperature; Value: 13
bitfield32 | DCEvt |  |  | Name: MEMORY_LOSS; Label: Memory Loss; Value: 14
bitfield32 | DCEvt |  |  | Name: ARC_DETECTION; Label: Arc Detection; Value: 15
bitfield32 | DCEvt |  |  | Name: TEST_FAILED; Label: Test Failed; Value: 20
bitfield32 | DCEvt |  |  | Name: INPUT_UNDER_VOLTAGE; Label: Under Voltage; Value: 21
bitfield32 | DCEvt |  |  | Name: INPUT_OVER_CURRENT; Label: Over Current; Value: 22

## 201
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Meter (Single Phase)single phase (AN or AB) meter | 201 | uint16 |  |  | R | M | Include this model for single phase (AN or AB) metering
Header |  | 1 |  | 1 | L |  | 105 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | A | Amps |  | int16 | A | A_SF | R | M | Total AC Current
Fixed Block |  | 3 | 1 | 1 | AphA | Amps PhaseA |  | int16 | A | A_SF | R | M | Phase A Current
Fixed Block |  | 4 | 2 | 1 | AphB | Amps PhaseB |  | int16 | A | A_SF | R | O | Phase B Current
Fixed Block |  | 5 | 3 | 1 | AphC | Amps PhaseC |  | int16 | A | A_SF | R | O | Phase C Current
Fixed Block |  | 6 | 4 | Size: 1; Name: A_SF; Type: sunssf; R/W: R | M | Current scale factor
Fixed Block |  | 7 | 5 | 1 | PhV | Voltage LN |  | int16 | V | V_SF | R | O | Line to Neutral AC Voltage (average of active phases) | Conditional AN connection
Fixed Block |  | 8 | 6 | 1 | PhVphA | Phase Voltage AN |  | int16 | V | V_SF | R | O | Phase Voltage AN | Conditional AN connection
Fixed Block |  | 9 | 7 | 1 | PhVphB | Phase Voltage BN |  | int16 | V | V_SF | R | O | Phase Voltage BN
Fixed Block |  | 10 | 8 | 1 | PhVphC | Phase Voltage CN |  | int16 | V | V_SF | R | O | Phase Voltage CN
Fixed Block |  | 11 | 9 | 1 | PPV | Voltage LL |  | int16 | V | V_SF | R | O | Line to Line AC Voltage (average of active phases)
Fixed Block |  | 12 | 10 | 1 | PPVphAB | Phase Voltage AB |  | int16 | V | V_SF | R | O | Phase Voltage AB | Conditional AB connection
Fixed Block |  | 13 | 11 | 1 | PPVphBC | Phase Voltage BC |  | int16 | V | V_SF | R | O | Phase Voltage BC
Fixed Block |  | 14 | 12 | 1 | PPVphCA | Phase Voltage CA |  | int16 | V | V_SF | R | O | Phase Voltage CA
Fixed Block |  | 15 | 13 | Size: 1; Name: V_SF; Type: sunssf; R/W: R | M | Voltage scale factor
Fixed Block |  | 16 | 14 | 1 | Hz | Hz |  | int16 | Hz | Hz_SF | R | M | Frequency
Fixed Block |  | 17 | 15 | Size: 1; Name: Hz_SF; Type: sunssf; R/W: R | O | Frequency scale factor
Fixed Block |  | 18 | 16 | 1 | W | Watts |  | int16 | W | W_SF | R | M | Total Real Power
Fixed Block |  | 19 | 17 | 1 | WphA | Watts phase A |  | int16 | W | W_SF | R | O
Fixed Block |  | 20 | 18 | 1 | WphB | Watts phase B |  | int16 | W | W_SF | R | O
Fixed Block |  | 21 | 19 | 1 | WphC | Watts phase C |  | int16 | W | W_SF | R | O
Fixed Block |  | 22 | 20 | Size: 1; Name: W_SF; Type: sunssf; R/W: R | M | Real Power scale factor
Fixed Block |  | 23 | 21 | 1 | VA | VA |  | int16 | VA | VA_SF | R | O | AC Apparent Power
Fixed Block |  | 24 | 22 | 1 | VAphA | VA phase A |  | int16 | VA | VA_SF | R | O
Fixed Block |  | 25 | 23 | 1 | VAphB | VA phase B |  | int16 | VA | VA_SF | R | O
Fixed Block |  | 26 | 24 | 1 | VAphC | VA phase C |  | int16 | VA | VA_SF | R | O
Fixed Block |  | 27 | 25 | Size: 1; Name: VA_SF; Type: sunssf; R/W: R | O | Apparent Power scale factor
Fixed Block |  | 28 | 26 | 1 | VAR | VAR |  | int16 | var | VAR_SF | R | O | Reactive Power
Fixed Block |  | 29 | 27 | 1 | VARphA | VAR phase A |  | int16 | var | VAR_SF | R | O
Fixed Block |  | 30 | 28 | 1 | VARphB | VAR phase B |  | int16 | var | VAR_SF | R | O
Fixed Block |  | 31 | 29 | 1 | VARphC | VAR phase C |  | int16 | var | VAR_SF | R | O
Fixed Block |  | 32 | 30 | Size: 1; Name: VAR_SF; Type: sunssf; R/W: R | O | Reactive Power scale factor
Fixed Block |  | 33 | 31 | 1 | PF | PF |  | int16 | Pct | PF_SF | R | O | Power Factor
Fixed Block |  | 34 | 32 | 1 | PFphA | PF phase A |  | int16 | Pct | PF_SF | R | O
Fixed Block |  | 35 | 33 | 1 | PFphB | PF phase B |  | int16 | Pct | PF_SF | R | O
Fixed Block |  | 36 | 34 | 1 | PFphC | PF phase C |  | int16 | Pct | PF_SF | R | O
Fixed Block |  | 37 | 35 | Size: 1; Name: PF_SF; Type: sunssf; R/W: R | O | Power Factor scale factor
Fixed Block |  | 38 | 36 | 2 | TotWhExp | Total Watt-hours Exported |  | acc32 | Wh | TotWh_SF | R | M | Total Real Energy Exported
Fixed Block |  | 40 | 38 | 2 | TotWhExpPhA | Total Watt-hours Exported phase A |  | acc32 | Wh | TotWh_SF | R | O
Fixed Block |  | 42 | 40 | 2 | TotWhExpPhB | Total Watt-hours Exported phase B |  | acc32 | Wh | TotWh_SF | R | O
Fixed Block |  | 44 | 42 | 2 | TotWhExpPhC | Total Watt-hours Exported phase C |  | acc32 | Wh | TotWh_SF | R | O
Fixed Block |  | 46 | 44 | 2 | TotWhImp | Total Watt-hours Imported |  | acc32 | Wh | TotWh_SF | R | M | Total Real Energy Imported
Fixed Block |  | 48 | 46 | 2 | TotWhImpPhA | Total Watt-hours Imported phase A |  | acc32 | Wh | TotWh_SF | R | O
Fixed Block |  | 50 | 48 | 2 | TotWhImpPhB | Total Watt-hours Imported phase B |  | acc32 | Wh | TotWh_SF | R | O
Fixed Block |  | 52 | 50 | 2 | TotWhImpPhC | Total Watt-hours Imported phase C |  | acc32 | Wh | TotWh_SF | R | O
Fixed Block |  | 54 | 52 | Size: 1; Name: TotWh_SF; Type: sunssf; R/W: R | M | Real Energy scale factor
Fixed Block |  | 55 | 53 | 2 | TotVAhExp | Total VA-hours Exported |  | acc32 | VAh | TotVAh_SF | R | O | Total Apparent Energy Exported
Fixed Block |  | 57 | 55 | 2 | TotVAhExpPhA | Total VA-hours Exported phase A |  | acc32 | VAh | TotVAh_SF | R | O
Fixed Block |  | 59 | 57 | 2 | TotVAhExpPhB | Total VA-hours Exported phase B |  | acc32 | VAh | TotVAh_SF | R | O
Fixed Block |  | 61 | 59 | 2 | TotVAhExpPhC | Total VA-hours Exported phase C |  | acc32 | VAh | TotVAh_SF | R | O
Fixed Block |  | 63 | 61 | 2 | TotVAhImp | Total VA-hours Imported |  | acc32 | VAh | TotVAh_SF | R | O | Total Apparent Energy Imported
Fixed Block |  | 65 | 63 | 2 | TotVAhImpPhA | Total VA-hours Imported phase A |  | acc32 | VAh | TotVAh_SF | R | O
Fixed Block |  | 67 | 65 | 2 | TotVAhImpPhB | Total VA-hours Imported phase B |  | acc32 | VAh | TotVAh_SF | R | O
Fixed Block |  | 69 | 67 | 2 | TotVAhImpPhC | Total VA-hours Imported phase C |  | acc32 | VAh | TotVAh_SF | R | O
Fixed Block |  | 71 | 69 | Size: 1; Name: TotVAh_SF; Type: sunssf; R/W: R | O | Apparent Energy scale factor
Fixed Block |  | 72 | 70 | 2 | TotVArhImpQ1 | Total VAR-hours Imported Q1 |  | acc32 | varh | TotVArh_SF | R | O | Total Reactive Energy Imported Quadrant 1
Fixed Block |  | 74 | 72 | 2 | TotVArhImpQ1PhA | Total VAr-hours Imported Q1 phase A |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 76 | 74 | 2 | TotVArhImpQ1PhB | Total VAr-hours Imported Q1 phase B |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 78 | 76 | 2 | TotVArhImpQ1PhC | Total VAr-hourse Imported Q1 phase C |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 80 | 78 | 2 | TotVArhImpQ2 | Total VAr-hours Imported Q2 |  | acc32 | varh | TotVArh_SF | R | O | Total Reactive Power Imported Quadrant 2
Fixed Block |  | 82 | 80 | 2 | TotVArhImpQ2PhA | Total VAr-hours Imported Q2 phase A |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 84 | 82 | 2 | TotVArhImpQ2PhB | Total VAr-hours Imported Q2 phase B |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 86 | 84 | 2 | TotVArhImpQ2PhC | Total VAr-hours Imported Q2 phase C |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 88 | 86 | 2 | TotVArhExpQ3 | Total VAr-hours Exported Q3 |  | acc32 | varh | TotVArh_SF | R | O | Total Reactive Power Exported Quadrant 3
Fixed Block |  | 90 | 88 | 2 | TotVArhExpQ3PhA | Total VAr-hours Exported Q3 phase A |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 92 | 90 | 2 | TotVArhExpQ3PhB | Total VAr-hours Exported Q3 phase B |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 94 | 92 | 2 | TotVArhExpQ3PhC | Total VAr-hours Exported Q3 phase C |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 96 | 94 | 2 | TotVArhExpQ4 | Total VAr-hours Exported Q4 |  | acc32 | varh | TotVArh_SF | R | O | Total Reactive Power Exported Quadrant 4
Fixed Block |  | 98 | 96 | 2 | TotVArhExpQ4PhA | Total VAr-hours Exported Q4 Imported phase A |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 100 | 98 | 2 | TotVArhExpQ4PhB |  |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 102 | 100 | 2 | TotVArhExpQ4PhC | Total VAr-hours Exported Q4 Imported phase C |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 104 | 102 | Size: 1; Name: TotVArh_SF; Type: sunssf; R/W: R | O | Reactive Energy scale factor
Fixed Block |  | 105 | 103 | 2 | Evt | Events |  | bitfield32 |  |  | R | M | Meter Event Flags
bitfield32 | Evt |  |  | Name: Power_Failure; Label: Power Failure; Value: 2 |  | Loss of power or phase
bitfield32 | Evt |  |  | Name: Under_Voltage; Label: Under Voltage; Value: 3 |  | Voltage below threshold (Phase Loss)
bitfield32 | Evt |  |  | Name: Low_PF; Label: Low PF; Value: 4 |  | Power Factor below threshold
bitfield32 | Evt |  |  | Name: Over_Current; Label: Over Current; Value: 5 |  | Current Input over threshold
bitfield32 | Evt |  |  | Name: Over_Voltage; Label: Over Voltage; Value: 6 |  | Voltage Input over threshold
bitfield32 | Evt |  |  | Name: Missing_Sensor; Label: Missing Sensor; Value: 7 |  | Sensor not connected
bitfield32 | Evt |  |  | Name: OEM01; Label: OEM01; Value: 16 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Name: OEM02; Label: OEM02; Value: 17 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Name: OEM03; Label: OEM01; Value: 18 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Name: OEM04; Label: OEM04; Value: 19 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Name: OEM05; Label: OEM05; Value: 20 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Name: OEM06; Label: OEM06; Value: 21 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Name: OEM07; Label: OEM07; Value: 22 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Name: OEM08; Label: OEM08; Value: 23 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Name: OEM09; Label: OEM09; Value: 24 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Name: OEM10; Label: OEM10; Value: 25 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Name: OEM11; Label: OEM11; Value: 26 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Name: OEM12; Label: OEM12; Value: 27 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Name: OEM13; Label: OEM13; Value: 28 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Name: OEM14; Label: OEM14; Value: 29 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Name: OEM15; Label: OEM15; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM16; Value: 30 |  | Reserved for OEM use

## 202
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | split single phase (ABN) meter | 202 | uint16 |  |  | R | M
Header |  | 1 |  | 1 | L |  | 105 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | A | Amps |  | int16 | A | A_SF | R | M | Total AC Current
Fixed Block |  | 3 | 1 | 1 | AphA | Amps PhaseA |  | int16 | A | A_SF | R | O | Phase A Current
Fixed Block |  | 4 | 2 | 1 | AphB | Amps PhaseB |  | int16 | A | A_SF | R | M | Phase B Current
Fixed Block |  | 5 | 3 | 1 | AphC | Amps PhaseC |  | int16 | A | A_SF | R | M | Phase C Current
Fixed Block |  | 6 | 4 | Size: 1; Name: A_SF; Type: sunssf; R/W: R | M | Current scale factor
Fixed Block |  | 7 | 5 | 1 | PhV | Voltage LN |  | int16 | V | V_SF | R | M | Line to Neutral AC Voltage (average of active phases)
Fixed Block |  | 8 | 6 | 1 | PhVphA | Phase Voltage AN |  | int16 | V | V_SF | R | M | Phase Voltage AN
Fixed Block |  | 9 | 7 | 1 | PhVphB | Phase Voltage BN |  | int16 | V | V_SF | R | M | Phase Voltage BN
Fixed Block |  | 10 | 8 | 1 | PhVphC | Phase Voltage CN |  | int16 | V | V_SF | R | O | Phase Voltage CN
Fixed Block |  | 11 | 9 | 1 | PPV | Voltage LL |  | int16 | V | V_SF | R | M | Line to Line AC Voltage (average of active phases)
Fixed Block |  | 12 | 10 | 1 | PhVphAB |  |  | int16 | V | V_SF | R | M
Fixed Block |  | 13 | 11 | 1 | PhVphBC |  |  | int16 | V | V_SF | R | O
Fixed Block |  | 14 | 12 | 1 | PhVphCA |  |  | int16 | V | V_SF | R | O
Fixed Block |  | 15 | 13 | Size: 1; Name: V_SF; Type: sunssf; R/W: R | M | Voltage scale factor
Fixed Block |  | 16 | 14 | 1 | Hz | Hz |  | int16 | Hz | Hz_SF | R | M | Frequency
Fixed Block |  | 17 | 15 | Size: 1; Name: Hz_SF; Type: sunssf; R/W: R | O | Frequency scale factor
Fixed Block |  | 18 | 16 | 1 | W | Watts |  | int16 | W | W_SF | R | M | Total Real Power
Fixed Block |  | 19 | 17 | 1 | WphA | Watts phase A |  | int16 | W | W_SF | R | O
Fixed Block |  | 20 | 18 | 1 | WphB | Watts phase B |  | int16 | W | W_SF | R | O
Fixed Block |  | 21 | 19 | 1 | WphC | Watts phase C |  | int16 | W | W_SF | R | O
Fixed Block |  | 22 | 20 | Size: 1; Name: W_SF; Type: sunssf; R/W: R | M | Real Power scale factor
Fixed Block |  | 23 | 21 | 1 | VA | VA |  | int16 | VA | VA_SF | R | O | AC Apparent Power
Fixed Block |  | 24 | 22 | 1 | VAphA | VA phase A |  | int16 | VA | VA_SF | R | O
Fixed Block |  | 25 | 23 | 1 | VAphB | VA phase B |  | int16 | VA | VA_SF | R | O
Fixed Block |  | 26 | 24 | 1 | VAphC | VA phase C |  | int16 | VA | VA_SF | R | O
Fixed Block |  | 27 | 25 | Size: 1; Name: VA_SF; Type: sunssf; R/W: R | O | Apparent Power scale factor
Fixed Block |  | 28 | 26 | 1 | VAR | VAR |  | int16 | var | VAR_SF | R | O | Reactive Power
Fixed Block |  | 29 | 27 | 1 | VARphA | VAR phase A |  | int16 | var | VAR_SF | R | O
Fixed Block |  | 30 | 28 | 1 | VARphB | VAR phase B |  | int16 | var | VAR_SF | R | O
Fixed Block |  | 31 | 29 | 1 | VARphC | VAR phase C |  | int16 | var | VAR_SF | R | O
Fixed Block |  | 32 | 30 | Size: 1; Name: VAR_SF; Type: sunssf; R/W: R | O | Reactive Power scale factor
Fixed Block |  | 33 | 31 | 1 | PF | PF |  | int16 | Pct | PF_SF | R | O | Power Factor
Fixed Block |  | 34 | 32 | 1 | PFphA | PF phase A |  | int16 | Pct | PF_SF | R | O
Fixed Block |  | 35 | 33 | 1 | PFphB | PF phase B |  | int16 | Pct | PF_SF | R | O
Fixed Block |  | 36 | 34 | 1 | PFphC | PF phase C |  | int16 | Pct | PF_SF | R | O
Fixed Block |  | 37 | 35 | Size: 1; Name: PF_SF; Type: sunssf; R/W: R | O | Power Factor scale factor
Fixed Block |  | 38 | 36 | 2 | TotWhExp | Total Watt-hours Exported |  | acc32 | Wh | TotWh_SF | R | M | Total Real Energy Exported
Fixed Block |  | 40 | 38 | 2 | TotWhExpPhA | Total Watt-hours Exported phase A |  | acc32 | Wh | TotWh_SF | R | O
Fixed Block |  | 42 | 40 | 2 | TotWhExpPhB | Total Watt-hours Exported phase B |  | acc32 | Wh | TotWh_SF | R | O
Fixed Block |  | 44 | 42 | 2 | TotWhExpPhC | Total Watt-hours Exported phase C |  | acc32 | Wh | TotWh_SF | R | O
Fixed Block |  | 46 | 44 | 2 | TotWhImp | Total Watt-hours Imported |  | acc32 | Wh | TotWh_SF | R | M | Total Real Energy Imported
Fixed Block |  | 48 | 46 | 2 | TotWhImpPhA | Total Watt-hours Imported phase A |  | acc32 | Wh | TotWh_SF | R | O
Fixed Block |  | 50 | 48 | 2 | TotWhImpPhB | Total Watt-hours Imported phase B |  | acc32 | Wh | TotWh_SF | R | O
Fixed Block |  | 52 | 50 | 2 | TotWhImpPhC | Total Watt-hours Imported phase C |  | acc32 | Wh | TotWh_SF | R | O
Fixed Block |  | 54 | 52 | Size: 1; Name: TotWh_SF; Type: sunssf; R/W: R | M | Real Energy scale factor
Fixed Block |  | 55 | 53 | 2 | TotVAhExp | Total VA-hours Exported |  | acc32 | VAh | TotVAh_SF | R | O | Total Apparent Energy Exported
Fixed Block |  | 57 | 55 | 2 | TotVAhExpPhA | Total VA-hours Exported phase A |  | acc32 | VAh | TotVAh_SF | R | O
Fixed Block |  | 59 | 57 | 2 | TotVAhExpPhB | Total VA-hours Exported phase B |  | acc32 | VAh | TotVAh_SF | R | O
Fixed Block |  | 61 | 59 | 2 | TotVAhExpPhC | Total VA-hours Exported phase C |  | acc32 | VAh | TotVAh_SF | R | O
Fixed Block |  | 63 | 61 | 2 | TotVAhImp | Total VA-hours Imported |  | acc32 | VAh | TotVAh_SF | R | O | Total Apparent Energy Imported
Fixed Block |  | 65 | 63 | 2 | TotVAhImpPhA | Total VA-hours Imported phase A |  | acc32 | VAh | TotVAh_SF | R | O
Fixed Block |  | 67 | 65 | 2 | TotVAhImpPhB | Total VA-hours Imported phase B |  | acc32 | VAh | TotVAh_SF | R | O
Fixed Block |  | 69 | 67 | 2 | TotVAhImpPhC | Total VA-hours Imported phase C |  | acc32 | VAh | TotVAh_SF | R | O
Fixed Block |  | 71 | 69 | Size: 1; Name: TotVAh_SF; Type: sunssf; R/W: R | O | Apparent Energy scale factor
Fixed Block |  | 72 | 70 | 2 | TotVArhImpQ1 | Total VAR-hours Imported Q1 |  | acc32 | varh | TotVArh_SF | R | O | Total Reactive Energy Imported Quadrant 1
Fixed Block |  | 74 | 72 | 2 | TotVArhImpQ1PhA | Total VAr-hours Imported Q1 phase A |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 76 | 74 | 2 | TotVArhImpQ1PhB | Total VAr-hours Imported Q1 phase B |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 78 | 76 | 2 | TotVArhImpQ1PhC | Total VAr-hourse Imported Q1 phase C |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 80 | 78 | 2 | TotVArhImpQ2 | Total VAr-hours Imported Q2 |  | acc32 | varh | TotVArh_SF | R | O | Total Reactive Power Imported Quadrant 2
Fixed Block |  | 82 | 80 | 2 | TotVArhImpQ2PhA | Total VAr-hours Imported Q2 phase A |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 84 | 82 | 2 | TotVArhImpQ2PhB | Total VAr-hours Imported Q2 phase B |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 86 | 84 | 2 | TotVArhImpQ2PhC | Total VAr-hours Imported Q2 phase C |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 88 | 86 | 2 | TotVArhExpQ3 | Total VAr-hours Exported Q3 |  | acc32 | varh | TotVArh_SF | R | O | Total Reactive Power Exported Quadrant 3
Fixed Block |  | 90 | 88 | 2 | TotVArhExpQ3PhA | Total VAr-hours Exported Q3 phase A |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 92 | 90 | 2 | TotVArhExpQ3PhB | Total VAr-hours Exported Q3 phase B |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 94 | 92 | 2 | TotVArhExpQ3PhC | Total VAr-hours Exported Q3 phase C |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 96 | 94 | 2 | TotVArhExpQ4 | Total VAr-hours Exported Q4 |  | acc32 | varh | TotVArh_SF | R | O | Total Reactive Power Exported Quadrant 4
Fixed Block |  | 98 | 96 | 2 | TotVArhExpQ4PhA | Total VAr-hours Exported Q4 Imported phase A |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 100 | 98 | 2 | TotVArhExpQ4PhB | Total VAr-hours Exported Q4 Imported phase B |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 102 | 100 | 2 | TotVArhExpQ4PhC | Total VAr-hours Exported Q4 Imported phase C |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 104 | 102 | Size: 1; Name: TotVArh_SF; Type: sunssf; R/W: R | O | Reactive Energy scale factor
Fixed Block |  | 105 | 103 | 2 | Evt | Events |  | bitfield32 |  |  | R | M | Meter Event Flags
bitfield32 | Evt |  |  | Name: M_EVENT_Power_Failure; Value: 2
bitfield32 | Evt |  |  | Name: M_EVENT_Under_Voltage; Value: 3
bitfield32 | Evt |  |  | Name: M_EVENT_Low_PF; Value: 4
bitfield32 | Evt |  |  | Name: M_EVENT_Over_Current; Value: 5
bitfield32 | Evt |  |  | Name: M_EVENT_Over_Voltage; Value: 6
bitfield32 | Evt |  |  | Name: M_EVENT_Missing_Sensor; Value: 7
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved1; Value: 8
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved2; Value: 9
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved3; Value: 10
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved4; Value: 11
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved5; Value: 12
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved6; Value: 13
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved7; Value: 14
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved8; Value: 15
bitfield32 | Evt |  |  | Name: M_EVENT_OEM01; Value: 16
bitfield32 | Evt |  |  | Name: M_EVENT_OEM02; Value: 17
bitfield32 | Evt |  |  | Name: M_EVENT_OEM03; Value: 18
bitfield32 | Evt |  |  | Name: M_EVENT_OEM04; Value: 19
bitfield32 | Evt |  |  | Name: M_EVENT_OEM05; Value: 20
bitfield32 | Evt |  |  | Name: M_EVENT_OEM06; Value: 21
bitfield32 | Evt |  |  | Name: M_EVENT_OEM07; Value: 22
bitfield32 | Evt |  |  | Name: M_EVENT_OEM08; Value: 23
bitfield32 | Evt |  |  | Name: M_EVENT_OEM09; Value: 24
bitfield32 | Evt |  |  | Name: M_EVENT_OEM10; Value: 25
bitfield32 | Evt |  |  | Name: M_EVENT_OEM11; Value: 26
bitfield32 | Evt |  |  | Name: M_EVENT_OEM12; Value: 27
bitfield32 | Evt |  |  | Name: M_EVENT_OEM13; Value: 28
bitfield32 | Evt |  |  | Name: M_EVENT_OEM14; Value: 29
bitfield32 | Evt |  |  | Name: M_EVENT_OEM15; Value: 30
bitfield32 | Evt |  |  | Label: Power Failure; Value: 30 |  | Loss of power or phase
bitfield32 | Evt |  |  | Label: Under Voltage; Value: 30 |  | Voltage below threshold (Phase Loss)
bitfield32 | Evt |  |  | Label: Low PF; Value: 30 |  | Power Factor below threshold
bitfield32 | Evt |  |  | Label: Over Current; Value: 30 |  | Current Input over threshold
bitfield32 | Evt |  |  | Label: Over Voltage; Value: 30 |  | Voltage Input over threshold
bitfield32 | Evt |  |  | Label: Missing Sensor; Value: 30 |  | Sensor not connected
bitfield32 | Evt |  |  | Label: OEM01; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM02; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM01; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM04; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM05; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM06; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM07; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM08; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM09; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM10; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM11; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM12; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM13; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM14; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM15; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM16; Value: 30 |  | Reserved for OEM use

## 203
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | wye-connect three phase (abcn) meter | 203 | uint16 |  |  | R | M
Header |  | 1 |  | 1 | L |  | 105 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | A | Amps |  | int16 | A | A_SF | R | M | Total AC Current
Fixed Block |  | 3 | 1 | 1 | AphA | Amps PhaseA |  | int16 | A | A_SF | R | M | Phase A Current
Fixed Block |  | 4 | 2 | 1 | AphB | Amps PhaseB |  | int16 | A | A_SF | R | M | Phase B Current
Fixed Block |  | 5 | 3 | 1 | AphC | Amps PhaseC |  | int16 | A | A_SF | R | M | Phase C Current
Fixed Block |  | 6 | 4 | Size: 1; Name: A_SF; Type: sunssf; R/W: R | M | Current scale factor
Fixed Block |  | 7 | 5 | 1 | PhV | Voltage LN |  | int16 | V | V_SF | R | M | Line to Neutral AC Voltage (average of active phases)
Fixed Block |  | 8 | 6 | 1 | PhVphA | Phase Voltage AN |  | int16 | V | V_SF | R | M | Phase Voltage AN
Fixed Block |  | 9 | 7 | 1 | PhVphB | Phase Voltage BN |  | int16 | V | V_SF | R | M | Phase Voltage BN
Fixed Block |  | 10 | 8 | 1 | PhVphC | Phase Voltage CN |  | int16 | V | V_SF | R | M | Phase Voltage CN
Fixed Block |  | 11 | 9 | 1 | PPV | Voltage LL |  | int16 | V | V_SF | R | M | Line to Line AC Voltage (average of active phases)
Fixed Block |  | 12 | 10 | 1 | PhVphAB |  |  | int16 | V | V_SF | R | M
Fixed Block |  | 13 | 11 | 1 | PhVphBC |  |  | int16 | V | V_SF | R | M
Fixed Block |  | 14 | 12 | 1 | PhVphCA |  |  | int16 | V | V_SF | R | M
Fixed Block |  | 15 | 13 | Size: 1; Name: V_SF; Type: sunssf; R/W: R | M | Voltage scale factor
Fixed Block |  | 16 | 14 | 1 | Hz | Hz |  | int16 | Hz | Hz_SF | R | M | Frequency
Fixed Block |  | 17 | 15 | Size: 1; Name: Hz_SF; Type: sunssf; R/W: R | O | Frequency scale factor
Fixed Block |  | 18 | 16 | 1 | W | Watts |  | int16 | W | W_SF | R | M | Total Real Power
Fixed Block |  | 19 | 17 | 1 | WphA | Watts phase A |  | int16 | W | W_SF | R | O
Fixed Block |  | 20 | 18 | 1 | WphB | Watts phase B |  | int16 | W | W_SF | R | O
Fixed Block |  | 21 | 19 | 1 | WphC | Watts phase C |  | int16 | W | W_SF | R | O
Fixed Block |  | 22 | 20 | Size: 1; Name: W_SF; Type: sunssf; R/W: R | M | Real Power scale factor
Fixed Block |  | 23 | 21 | 1 | VA | VA |  | int16 | VA | VA_SF | R | O | AC Apparent Power
Fixed Block |  | 24 | 22 | 1 | VAphA | VA phase A |  | int16 | VA | VA_SF | R | O
Fixed Block |  | 25 | 23 | 1 | VAphB | VA phase B |  | int16 | VA | VA_SF | R | O
Fixed Block |  | 26 | 24 | 1 | VAphC | VA phase C |  | int16 | VA | VA_SF | R | O
Fixed Block |  | 27 | 25 | Size: 1; Name: VA_SF; Type: sunssf; R/W: R | O | Apparent Power scale factor
Fixed Block |  | 28 | 26 | 1 | VAR | VAR |  | int16 | var | VAR_SF | R | O | Reactive Power
Fixed Block |  | 29 | 27 | 1 | VARphA | VAR phase A |  | int16 | var | VAR_SF | R | O
Fixed Block |  | 30 | 28 | 1 | VARphB | VAR phase B |  | int16 | var | VAR_SF | R | O
Fixed Block |  | 31 | 29 | 1 | VARphC | VAR phase C |  | int16 | var | VAR_SF | R | O
Fixed Block |  | 32 | 30 | Size: 1; Name: VAR_SF; Type: sunssf; R/W: R | O | Reactive Power scale factor
Fixed Block |  | 33 | 31 | 1 | PF | PF |  | int16 | Pct | PF_SF | R | O | Power Factor
Fixed Block |  | 34 | 32 | 1 | PFphA | PF phase A |  | int16 | Pct | PF_SF | R | O
Fixed Block |  | 35 | 33 | 1 | PFphB | PF phase B |  | int16 | Pct | PF_SF | R | O
Fixed Block |  | 36 | 34 | 1 | PFphC | PF phase C |  | int16 | Pct | PF_SF | R | O
Fixed Block |  | 37 | 35 | Size: 1; Name: PF_SF; Type: sunssf; R/W: R | O | Power Factor scale factor
Fixed Block |  | 38 | 36 | 2 | TotWhExp | Total Watt-hours Exported |  | acc32 | Wh | TotWh_SF | R | M | Total Real Energy Exported
Fixed Block |  | 40 | 38 | 2 | TotWhExpPhA | Total Watt-hours Exported phase A |  | acc32 | Wh | TotWh_SF | R | O
Fixed Block |  | 42 | 40 | 2 | TotWhExpPhB | Total Watt-hours Exported phase B |  | acc32 | Wh | TotWh_SF | R | O
Fixed Block |  | 44 | 42 | 2 | TotWhExpPhC | Total Watt-hours Exported phase C |  | acc32 | Wh | TotWh_SF | R | O
Fixed Block |  | 46 | 44 | 2 | TotWhImp | Total Watt-hours Imported |  | acc32 | Wh | TotWh_SF | R | M | Total Real Energy Imported
Fixed Block |  | 48 | 46 | 2 | TotWhImpPhA | Total Watt-hours Imported phase A |  | acc32 | Wh | TotWh_SF | R | O
Fixed Block |  | 50 | 48 | 2 | TotWhImpPhB | Total Watt-hours Imported phase B |  | acc32 | Wh | TotWh_SF | R | O
Fixed Block |  | 52 | 50 | 2 | TotWhImpPhC | Total Watt-hours Imported phase C |  | acc32 | Wh | TotWh_SF | R | O
Fixed Block |  | 54 | 52 | Size: 1; Name: TotWh_SF; Type: sunssf; R/W: R | M | Real Energy scale factor
Fixed Block |  | 55 | 53 | 2 | TotVAhExp | Total VA-hours Exported |  | acc32 | VAh | TotVAh_SF | R | O | Total Apparent Energy Exported
Fixed Block |  | 57 | 55 | 2 | TotVAhExpPhA | Total VA-hours Exported phase A |  | acc32 | VAh | TotVAh_SF | R | O
Fixed Block |  | 59 | 57 | 2 | TotVAhExpPhB | Total VA-hours Exported phase B |  | acc32 | VAh | TotVAh_SF | R | O
Fixed Block |  | 61 | 59 | 2 | TotVAhExpPhC | Total VA-hours Exported phase C |  | acc32 | VAh | TotVAh_SF | R | O
Fixed Block |  | 63 | 61 | 2 | TotVAhImp | Total VA-hours Imported |  | acc32 | VAh | TotVAh_SF | R | O | Total Apparent Energy Imported
Fixed Block |  | 65 | 63 | 2 | TotVAhImpPhA | Total VA-hours Imported phase A |  | acc32 | VAh | TotVAh_SF | R | O
Fixed Block |  | 67 | 65 | 2 | TotVAhImpPhB | Total VA-hours Imported phase B |  | acc32 | VAh | TotVAh_SF | R | O
Fixed Block |  | 69 | 67 | 2 | TotVAhImpPhC | Total VA-hours Imported phase C |  | acc32 | VAh | TotVAh_SF | R | O
Fixed Block |  | 71 | 69 | Size: 1; Name: TotVAh_SF; Type: sunssf; R/W: R | O | Apparent Energy scale factor
Fixed Block |  | 72 | 70 | 2 | TotVArhImpQ1 | Total VAR-hours Imported Q1 |  | acc32 | varh | TotVArh_SF | R | O | Total Reactive Energy Imported Quadrant 1
Fixed Block |  | 74 | 72 | 2 | TotVArhImpQ1PhA | Total VAr-hours Imported Q1 phase A |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 76 | 74 | 2 | TotVArhImpQ1PhB | Total VAr-hours Imported Q1 phase B |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 78 | 76 | 2 | TotVArhImpQ1PhC | Total VAr-hourse Imported Q1 phase C |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 80 | 78 | 2 | TotVArhImpQ2 | Total VAr-hours Imported Q2 |  | acc32 | varh | TotVArh_SF | R | O | Total Reactive Power Imported Quadrant 2
Fixed Block |  | 82 | 80 | 2 | TotVArhImpQ2PhA | Total VAr-hours Imported Q2 phase A |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 84 | 82 | 2 | TotVArhImpQ2PhB | Total VAr-hours Imported Q2 phase B |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 86 | 84 | 2 | TotVArhImpQ2PhC | Total VAr-hours Imported Q2 phase C |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 88 | 86 | 2 | TotVArhExpQ3 | Total VAr-hours Exported Q3 |  | acc32 | varh | TotVArh_SF | R | O | Total Reactive Power Exported Quadrant 3
Fixed Block |  | 90 | 88 | 2 | TotVArhExpQ3PhA | Total VAr-hours Exported Q3 phase A |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 92 | 90 | 2 | TotVArhExpQ3PhB | Total VAr-hours Exported Q3 phase B |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 94 | 92 | 2 | TotVArhExpQ3PhC | Total VAr-hours Exported Q3 phase C |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 96 | 94 | 2 | TotVArhExpQ4 | Total VAr-hours Exported Q4 |  | acc32 | varh | TotVArh_SF | R | O | Total Reactive Power Exported Quadrant 4
Fixed Block |  | 98 | 96 | 2 | TotVArhExpQ4PhA | Total VAr-hours Exported Q4 Imported phase A |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 100 | 98 | 2 | TotVArhExpQ4PhB |  |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 102 | 100 | 2 | TotVArhExpQ4PhC | Total VAr-hours Exported Q4 Imported phase C |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 104 | 102 | Size: 1; Name: TotVArh_SF; Type: sunssf; R/W: R | O | Reactive Energy scale factor
Fixed Block |  | 105 | 103 | 2 | Evt | Events |  | bitfield32 |  |  | R | M | Meter Event Flags
bitfield32 | Evt |  |  | Name: M_EVENT_Power_Failure; Value: 2
bitfield32 | Evt |  |  | Name: M_EVENT_Under_Voltage; Value: 3
bitfield32 | Evt |  |  | Name: M_EVENT_Low_PF; Value: 4
bitfield32 | Evt |  |  | Name: M_EVENT_Over_Current; Value: 5
bitfield32 | Evt |  |  | Name: M_EVENT_Over_Voltage; Value: 6
bitfield32 | Evt |  |  | Name: M_EVENT_Missing_Sensor; Value: 7
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved1; Value: 8
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved2; Value: 9
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved3; Value: 10
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved4; Value: 11
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved5; Value: 12
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved6; Value: 13
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved7; Value: 14
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved8; Value: 15
bitfield32 | Evt |  |  | Name: M_EVENT_OEM01; Value: 16
bitfield32 | Evt |  |  | Name: M_EVENT_OEM02; Value: 17
bitfield32 | Evt |  |  | Name: M_EVENT_OEM03; Value: 18
bitfield32 | Evt |  |  | Name: M_EVENT_OEM04; Value: 19
bitfield32 | Evt |  |  | Name: M_EVENT_OEM05; Value: 20
bitfield32 | Evt |  |  | Name: M_EVENT_OEM06; Value: 21
bitfield32 | Evt |  |  | Name: M_EVENT_OEM07; Value: 22
bitfield32 | Evt |  |  | Name: M_EVENT_OEM08; Value: 23
bitfield32 | Evt |  |  | Name: M_EVENT_OEM09; Value: 24
bitfield32 | Evt |  |  | Name: M_EVENT_OEM10; Value: 25
bitfield32 | Evt |  |  | Name: M_EVENT_OEM11; Value: 26
bitfield32 | Evt |  |  | Name: M_EVENT_OEM12; Value: 27
bitfield32 | Evt |  |  | Name: M_EVENT_OEM13; Value: 28
bitfield32 | Evt |  |  | Name: M_EVENT_OEM14; Value: 29
bitfield32 | Evt |  |  | Name: M_EVENT_OEM15; Value: 30
bitfield32 | Evt |  |  | Label: Power Failure; Value: 30 |  | Loss of power or phase
bitfield32 | Evt |  |  | Label: Under Voltage; Value: 30 |  | Voltage below threshold (Phase Loss)
bitfield32 | Evt |  |  | Label: Low PF; Value: 30 |  | Power Factor below threshold
bitfield32 | Evt |  |  | Label: Over Current; Value: 30 |  | Current Input over threshold
bitfield32 | Evt |  |  | Label: Over Voltage; Value: 30 |  | Voltage Input over threshold
bitfield32 | Evt |  |  | Label: Missing Sensor; Value: 30 |  | Sensor not connected
bitfield32 | Evt |  |  | Label: OEM01; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM02; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM01; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM04; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM05; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM06; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM07; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM08; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM09; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM10; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM11; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM12; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM13; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM14; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM15; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM16; Value: 30 |  | Reserved for OEM use

## 204
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | delta-connect three phase (abc) meter | 204 | uint16 |  |  | R | M
Header |  | 1 |  | 1 | L |  | 105 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | A | Amps |  | int16 | A | A_SF | R | M | Total AC Current
Fixed Block |  | 3 | 1 | 1 | AphA | Amps PhaseA |  | int16 | A | A_SF | R | M | Phase A Current
Fixed Block |  | 4 | 2 | 1 | AphB | Amps PhaseB |  | int16 | A | A_SF | R | M | Phase B Current
Fixed Block |  | 5 | 3 | 1 | AphC | Amps PhaseC |  | int16 | A | A_SF | R | M | Phase C Current
Fixed Block |  | 6 | 4 | Size: 1; Name: A_SF; Type: sunssf; R/W: R | M | Current scale factor
Fixed Block |  | 7 | 5 | 1 | PhV | Voltage LN |  | int16 | V | V_SF | R | O | Line to Neutral AC Voltage (average of active phases)
Fixed Block |  | 8 | 6 | 1 | PhVphA | Phase Voltage AN |  | int16 | V | V_SF | R | O | Phase Voltage AN
Fixed Block |  | 9 | 7 | 1 | PhVphB | Phase Voltage BN |  | int16 | V | V_SF | R | O | Phase Voltage BN
Fixed Block |  | 10 | 8 | 1 | PhVphC | Phase Voltage CN |  | int16 | V | V_SF | R | O | Phase Voltage CN
Fixed Block |  | 11 | 9 | 1 | PPV | Voltage LL |  | int16 | V | V_SF | R | M | Line to Line AC Voltage (average of active phases)
Fixed Block |  | 12 | 10 | 1 | PhVphAB |  |  | int16 | V | V_SF | R | M
Fixed Block |  | 13 | 11 | 1 | PhVphBC |  |  | int16 | V | V_SF | R | M
Fixed Block |  | 14 | 12 | 1 | PhVphCA |  |  | int16 | V | V_SF | R | M
Fixed Block |  | 15 | 13 | Size: 1; Name: V_SF; Type: sunssf; R/W: R | M | Voltage scale factor
Fixed Block |  | 16 | 14 | 1 | Hz | Hz |  | int16 | Hz | Hz_SF | R | M | Frequency
Fixed Block |  | 17 | 15 | Size: 1; Name: Hz_SF; Type: sunssf; R/W: R | O | Frequency scale factor
Fixed Block |  | 18 | 16 | 1 | W | Watts |  | int16 | W | W_SF | R | M | Total Real Power
Fixed Block |  | 19 | 17 | 1 | WphA | Watts phase A |  | int16 | W | W_SF | R | O
Fixed Block |  | 20 | 18 | 1 | WphB | Watts phase B |  | int16 | W | W_SF | R | O
Fixed Block |  | 21 | 19 | 1 | WphC | Watts phase C |  | int16 | W | W_SF | R | O
Fixed Block |  | 22 | 20 | Size: 1; Name: W_SF; Type: sunssf; R/W: R | M | Real Power scale factor
Fixed Block |  | 23 | 21 | 1 | VA | VA |  | int16 | VA | VA_SF | R | O | AC Apparent Power
Fixed Block |  | 24 | 22 | 1 | VAphA | VA phase A |  | int16 | VA | VA_SF | R | O
Fixed Block |  | 25 | 23 | 1 | VAphB | VA phase B |  | int16 | VA | VA_SF | R | O
Fixed Block |  | 26 | 24 | 1 | VAphC | VA phase C |  | int16 | VA | VA_SF | R | O
Fixed Block |  | 27 | 25 | Size: 1; Name: VA_SF; Type: sunssf; R/W: R | O | Apparent Power scale factor
Fixed Block |  | 28 | 26 | 1 | VAR | VAR |  | int16 | var | VAR_SF | R | O | Reactive Power
Fixed Block |  | 29 | 27 | 1 | VARphA | VAR phase A |  | int16 | var | VAR_SF | R | O
Fixed Block |  | 30 | 28 | 1 | VARphB | VAR phase B |  | int16 | var | VAR_SF | R | O
Fixed Block |  | 31 | 29 | 1 | VARphC | VAR phase C |  | int16 | var | VAR_SF | R | O
Fixed Block |  | 32 | 30 | Size: 1; Name: VAR_SF; Type: sunssf; R/W: R | O | Reactive Power scale factor
Fixed Block |  | 33 | 31 | 1 | PF | PF |  | int16 | Pct | PF_SF | R | O | Power Factor
Fixed Block |  | 34 | 32 | 1 | PFphA | PF phase A |  | int16 | Pct | PF_SF | R | O
Fixed Block |  | 35 | 33 | 1 | PFphB | PF phase B |  | int16 | Pct | PF_SF | R | O
Fixed Block |  | 36 | 34 | 1 | PFphC | PF phase C |  | int16 | Pct | PF_SF | R | O
Fixed Block |  | 37 | 35 | Size: 1; Name: PF_SF; Type: sunssf; R/W: R | O | Power Factor scale factor
Fixed Block |  | 38 | 36 | 2 | TotWhExp | Total Watt-hours Exported |  | acc32 | Wh | TotWh_SF | R | M | Total Real Energy Exported
Fixed Block |  | 40 | 38 | 2 | TotWhExpPhA | Total Watt-hours Exported phase A |  | acc32 | Wh | TotWh_SF | R | O
Fixed Block |  | 42 | 40 | 2 | TotWhExpPhB | Total Watt-hours Exported phase B |  | acc32 | Wh | TotWh_SF | R | O
Fixed Block |  | 44 | 42 | 2 | TotWhExpPhC | Total Watt-hours Exported phase C |  | acc32 | Wh | TotWh_SF | R | O
Fixed Block |  | 46 | 44 | 2 | TotWhImp | Total Watt-hours Imported |  | acc32 | Wh | TotWh_SF | R | M | Total Real Energy Imported
Fixed Block |  | 48 | 46 | 2 | TotWhImpPhA | Total Watt-hours Imported phase A |  | acc32 | Wh | TotWh_SF | R | O
Fixed Block |  | 50 | 48 | 2 | TotWhImpPhB | Total Watt-hours Imported phase B |  | acc32 | Wh | TotWh_SF | R | O
Fixed Block |  | 52 | 50 | 2 | TotWhImpPhC | Total Watt-hours Imported phase C |  | acc32 | Wh | TotWh_SF | R | O
Fixed Block |  | 54 | 52 | Size: 1; Name: TotWh_SF; Type: sunssf; R/W: R | M | Real Energy scale factor
Fixed Block |  | 55 | 53 | 2 | TotVAhExp | Total VA-hours Exported |  | acc32 | VAh | TotVAh_SF | R | O | Total Apparent Energy Exported
Fixed Block |  | 57 | 55 | 2 | TotVAhExpPhA | Total VA-hours Exported phase A |  | acc32 | VAh | TotVAh_SF | R | O
Fixed Block |  | 59 | 57 | 2 | TotVAhExpPhB | Total VA-hours Exported phase B |  | acc32 | VAh | TotVAh_SF | R | O
Fixed Block |  | 61 | 59 | 2 | TotVAhExpPhC | Total VA-hours Exported phase C |  | acc32 | VAh | TotVAh_SF | R | O
Fixed Block |  | 63 | 61 | 2 | TotVAhImp | Total VA-hours Imported |  | acc32 | VAh | TotVAh_SF | R | O | Total Apparent Energy Imported
Fixed Block |  | 65 | 63 | 2 | TotVAhImpPhA | Total VA-hours Imported phase A |  | acc32 | VAh | TotVAh_SF | R | O
Fixed Block |  | 67 | 65 | 2 | TotVAhImpPhB | Total VA-hours Imported phase B |  | acc32 | VAh | TotVAh_SF | R | O
Fixed Block |  | 69 | 67 | 2 | TotVAhImpPhC | Total VA-hours Imported phase C |  | acc32 | VAh | TotVAh_SF | R | O
Fixed Block |  | 71 | 69 | Size: 1; Name: TotVAh_SF; Type: sunssf; R/W: R | O | Apparent Energy scale factor
Fixed Block |  | 72 | 70 | 2 | TotVArhImpQ1 | Total VAR-hours Imported Q1 |  | acc32 | varh | TotVArh_SF | R | O | Total Reactive Energy Imported Quadrant 1
Fixed Block |  | 74 | 72 | 2 | TotVArhImpQ1PhA | Total VAr-hours Imported Q1 phase A |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 76 | 74 | 2 | TotVArhImpQ1PhB | Total VAr-hours Imported Q1 phase B |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 78 | 76 | 2 | TotVArhImpQ1PhC | Total VAr-hourse Imported Q1 phase C |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 80 | 78 | 2 | TotVArhImpQ2 | Total VAr-hours Imported Q2 |  | acc32 | varh | TotVArh_SF | R | O | Total Reactive Power Imported Quadrant 2
Fixed Block |  | 82 | 80 | 2 | TotVArhImpQ2PhA | Total VAr-hours Imported Q2 phase A |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 84 | 82 | 2 | TotVArhImpQ2PhB | Total VAr-hours Imported Q2 phase B |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 86 | 84 | 2 | TotVArhImpQ2PhC | Total VAr-hours Imported Q2 phase C |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 88 | 86 | 2 | TotVArhExpQ3 | Total VAr-hours Exported Q3 |  | acc32 | varh | TotVArh_SF | R | O | Total Reactive Power Exported Quadrant 3
Fixed Block |  | 90 | 88 | 2 | TotVArhExpQ3PhA | Total VAr-hours Exported Q3 phase A |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 92 | 90 | 2 | TotVArhExpQ3PhB | Total VAr-hours Exported Q3 phase B |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 94 | 92 | 2 | TotVArhExpQ3PhC | Total VAr-hours Exported Q3 phase C |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 96 | 94 | 2 | TotVArhExpQ4 | Total VAr-hours Exported Q4 |  | acc32 | varh | TotVArh_SF | R | O | Total Reactive Power Exported Quadrant 4
Fixed Block |  | 98 | 96 | 2 | TotVArhExpQ4PhA | Total VAr-hours Exported Q4 Imported phase A |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 100 | 98 | 2 | TotVArhExpQ4PhB |  |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 102 | 100 | 2 | TotVArhExpQ4PhC | Total VAr-hours Exported Q4 Imported phase C |  | acc32 | varh | TotVArh_SF | R | O
Fixed Block |  | 104 | 102 | Size: 1; Name: TotVArh_SF; Type: sunssf; R/W: R | O | Reactive Energy scale factor
Fixed Block |  | 105 | 103 | 2 | Evt | Events |  | bitfield32 |  |  | R | M | Meter Event Flags
bitfield32 | Evt |  |  | Name: M_EVENT_Power_Failure; Value: 2
bitfield32 | Evt |  |  | Name: M_EVENT_Under_Voltage; Value: 3
bitfield32 | Evt |  |  | Name: M_EVENT_Low_PF; Value: 4
bitfield32 | Evt |  |  | Name: M_EVENT_Over_Current; Value: 5
bitfield32 | Evt |  |  | Name: M_EVENT_Over_Voltage; Value: 6
bitfield32 | Evt |  |  | Name: M_EVENT_Missing_Sensor; Value: 7
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved1; Value: 8
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved2; Value: 9
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved3; Value: 10
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved4; Value: 11
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved5; Value: 12
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved6; Value: 13
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved7; Value: 14
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved8; Value: 15
bitfield32 | Evt |  |  | Name: M_EVENT_OEM01; Value: 16
bitfield32 | Evt |  |  | Name: M_EVENT_OEM02; Value: 17
bitfield32 | Evt |  |  | Name: M_EVENT_OEM03; Value: 18
bitfield32 | Evt |  |  | Name: M_EVENT_OEM04; Value: 19
bitfield32 | Evt |  |  | Name: M_EVENT_OEM05; Value: 20
bitfield32 | Evt |  |  | Name: M_EVENT_OEM06; Value: 21
bitfield32 | Evt |  |  | Name: M_EVENT_OEM07; Value: 22
bitfield32 | Evt |  |  | Name: M_EVENT_OEM08; Value: 23
bitfield32 | Evt |  |  | Name: M_EVENT_OEM09; Value: 24
bitfield32 | Evt |  |  | Name: M_EVENT_OEM10; Value: 25
bitfield32 | Evt |  |  | Name: M_EVENT_OEM11; Value: 26
bitfield32 | Evt |  |  | Name: M_EVENT_OEM12; Value: 27
bitfield32 | Evt |  |  | Name: M_EVENT_OEM13; Value: 28
bitfield32 | Evt |  |  | Name: M_EVENT_OEM14; Value: 29
bitfield32 | Evt |  |  | Name: M_EVENT_OEM15; Value: 30
bitfield32 | Evt |  |  | Label: Power Failure; Value: 30 |  | Loss of power or phase
bitfield32 | Evt |  |  | Label: Under Voltage; Value: 30 |  | Voltage below threshold (Phase Loss)
bitfield32 | Evt |  |  | Label: Low PF; Value: 30 |  | Power Factor below threshold
bitfield32 | Evt |  |  | Label: Over Current; Value: 30 |  | Current Input over threshold
bitfield32 | Evt |  |  | Label: Over Voltage; Value: 30 |  | Voltage Input over threshold
bitfield32 | Evt |  |  | Label: Missing Sensor; Value: 30 |  | Sensor not connected
bitfield32 | Evt |  |  | Label: OEM01; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM02; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM01; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM04; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM05; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM06; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM07; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM08; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM09; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM10; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM11; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM12; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM13; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM14; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM15; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM16; Value: 30 |  | Reserved for OEM use

## 211
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | single phase (AN or AB) meter | 211 | uint16 |  |  | R | M |  | Float
Header |  | 1 |  | 1 | L |  | 124 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 2 | A | Amps |  | float32 | A |  | R | M | Total AC Current
Fixed Block |  | 4 | 2 | 2 | AphA | Amps PhaseA |  | float32 | A |  | R | M | Phase A Current
Fixed Block |  | 6 | 4 | 2 | AphB | Amps PhaseB |  | float32 | A |  | R | O | Phase B Current
Fixed Block |  | 8 | 6 | 2 | AphC | Amps PhaseC |  | float32 | A |  | R | O | Phase C Current
Fixed Block |  | 10 | 8 | 2 | PhV | Voltage LN |  | float32 | V |  | R | O | Line to Neutral AC Voltage (average of active phases)
Fixed Block |  | 12 | 10 | 2 | PhVphA | Phase Voltage AN |  | float32 | V |  | R | O | Phase Voltage AN
Fixed Block |  | 14 | 12 | 2 | PhVphB | Phase Voltage BN |  | float32 | V |  | R | O | Phase Voltage BN
Fixed Block |  | 16 | 14 | 2 | PhVphC | Phase Voltage CN |  | float32 | V |  | R | O | Phase Voltage CN
Fixed Block |  | 18 | 16 | 2 | PPV | Voltage LL |  | float32 | V |  | R | O | Line to Line AC Voltage (average of active phases)
Fixed Block |  | 20 | 18 | 2 | PPVphAB | Phase Voltage AB |  | float32 | V |  | R | O | Phase Voltage AB
Fixed Block |  | 22 | 20 | 2 | PPVphBC | Phase Voltage BC |  | float32 | V |  | R | O | Phase Voltage BC
Fixed Block |  | 24 | 22 | 2 | PPVphCA | Phase Voltage CA |  | float32 | V |  | R | O | Phase Voltage CA
Fixed Block |  | 26 | 24 | 2 | Hz | Hz |  | float32 | Hz |  | R | M | Frequency
Fixed Block |  | 28 | 26 | 2 | W | Watts |  | float32 | W |  | R | M | Total Real Power
Fixed Block |  | 30 | 28 | 2 | WphA | Watts phase A |  | float32 | W |  | R | O
Fixed Block |  | 32 | 30 | 2 | WphB | Watts phase B |  | float32 | W |  | R | O
Fixed Block |  | 34 | 32 | 2 | WphC | Watts phase C |  | float32 | W |  | R | O
Fixed Block |  | 36 | 34 | 2 | VA | VA |  | float32 | VA |  | R | O | AC Apparent Power
Fixed Block |  | 38 | 36 | 2 | VAphA | VA phase A |  | float32 | VA |  | R | O
Fixed Block |  | 40 | 38 | 2 | VAphB | VA phase B |  | float32 | VA |  | R | O
Fixed Block |  | 42 | 40 | 2 | VAphC | VA phase C |  | float32 | VA |  | R | O
Fixed Block |  | 44 | 42 | 2 | VAR | VAR |  | float32 | var |  | R | O | Reactive Power
Fixed Block |  | 46 | 44 | 2 | VARphA | VAR phase A |  | float32 | var |  | R | O
Fixed Block |  | 48 | 46 | 2 | VARphB | VAR phase B |  | float32 | var |  | R | O
Fixed Block |  | 50 | 48 | 2 | VARphC | VAR phase C |  | float32 | var |  | R | O
Fixed Block |  | 52 | 50 | 2 | PF | PF |  | float32 | PF |  | R | O | Power Factor
Fixed Block |  | 54 | 52 | 2 | PFphA | PF phase A |  | float32 | PF |  | R | O
Fixed Block |  | 56 | 54 | 2 | PFphB | PF phase B |  | float32 | PF |  | R | O
Fixed Block |  | 58 | 56 | 2 | PFphC | PF phase C |  | float32 | PF |  | R | O
Fixed Block |  | 60 | 58 | 2 | TotWhExp | Total Watt-hours Exported |  | float32 | Wh |  | R | M | Total Real Energy Exported
Fixed Block |  | 62 | 60 | 2 | TotWhExpPhA | Total Watt-hours Exported phase A |  | float32 | Wh |  | R | O
Fixed Block |  | 64 | 62 | 2 | TotWhExpPhB | Total Watt-hours Exported phase B |  | float32 | Wh |  | R | O
Fixed Block |  | 66 | 64 | 2 | TotWhExpPhC | Total Watt-hours Exported phase C |  | float32 | Wh |  | R | O
Fixed Block |  | 68 | 66 | 2 | TotWhImp | Total Watt-hours Imported |  | float32 | Wh |  | R | M | Total Real Energy Imported
Fixed Block |  | 70 | 68 | 2 | TotWhImpPhA | Total Watt-hours Imported phase A |  | float32 | Wh |  | R | O
Fixed Block |  | 72 | 70 | 2 | TotWhImpPhB | Total Watt-hours Imported phase B |  | float32 | Wh |  | R | O
Fixed Block |  | 74 | 72 | 2 | TotWhImpPhC | Total Watt-hours Imported phase C |  | float32 | Wh |  | R | O
Fixed Block |  | 76 | 74 | 2 | TotVAhExp | Total VA-hours Exported |  | float32 | VAh |  | R | O | Total Apparent Energy Exported
Fixed Block |  | 78 | 76 | 2 | TotVAhExpPhA | Total VA-hours Exported phase A |  | float32 | VAh |  | R | O
Fixed Block |  | 80 | 78 | 2 | TotVAhExpPhB | Total VA-hours Exported phase B |  | float32 | VAh |  | R | O
Fixed Block |  | 82 | 80 | 2 | TotVAhExpPhC | Total VA-hours Exported phase C |  | float32 | VAh |  | R | O
Fixed Block |  | 84 | 82 | 2 | TotVAhImp | Total VA-hours Imported |  | float32 | VAh |  | R | O | Total Apparent Energy Imported
Fixed Block |  | 86 | 84 | 2 | TotVAhImpPhA | Total VA-hours Imported phase A |  | float32 | VAh |  | R | O
Fixed Block |  | 88 | 86 | 2 | TotVAhImpPhB | Total VA-hours Imported phase B |  | float32 | VAh |  | R | O
Fixed Block |  | 90 | 88 | 2 | TotVAhImpPhC | Total VA-hours Imported phase C |  | float32 | VAh |  | R | O
Fixed Block |  | 92 | 90 | 2 | TotVArhImpQ1 | Total VAR-hours Imported Q1 |  | float32 | varh |  | R | O | Total Reactive Energy Imported Quadrant 1
Fixed Block |  | 94 | 92 | 2 | TotVArhImpQ1phA |  |  | float32 | varh |  | R | O
Fixed Block |  | 96 | 94 | 2 | TotVArhImpQ1phB |  |  | float32 | varh |  | R | O
Fixed Block |  | 98 | 96 | 2 | TotVArhImpQ1phC |  |  | float32 | varh |  | R | O
Fixed Block |  | 100 | 98 | 2 | TotVArhImpQ2 | Total VAr-hours Imported Q2 |  | float32 | varh |  | R | O | Total Reactive Power Imported Quadrant 2
Fixed Block |  | 102 | 100 | 2 | TotVArhImpQ2phA |  |  | float32 | varh |  | R | O
Fixed Block |  | 104 | 102 | 2 | TotVArhImpQ2phB |  |  | float32 | varh |  | R | O
Fixed Block |  | 106 | 104 | 2 | TotVArhImpQ2phC |  |  | float32 | varh |  | R | O
Fixed Block |  | 108 | 106 | 2 | TotVArhExpQ3 | Total VAr-hours Exported Q3 |  | float32 | varh |  | R | O | Total Reactive Power Exported Quadrant 3
Fixed Block |  | 110 | 108 | 2 | TotVArhExpQ3phA |  |  | float32 | varh |  | R | O
Fixed Block |  | 112 | 110 | 2 | TotVArhExpQ3phB |  |  | float32 | varh |  | R | O
Fixed Block |  | 114 | 112 | 2 | TotVArhExpQ3phC |  |  | float32 | varh |  | R | O
Fixed Block |  | 116 | 114 | 2 | TotVArhExpQ4 | Total VAr-hours Exported Q4 |  | float32 | varh |  | R | O | Total Reactive Power Exported Quadrant 4
Fixed Block |  | 118 | 116 | 2 | TotVArhExpQ4phA |  |  | float32 | varh |  | R | O
Fixed Block |  | 120 | 118 | 2 | TotVArhExpQ4phB |  |  | float32 | varh |  | R | O
Fixed Block |  | 122 | 120 | 2 | TotVArhExpQ4phC |  |  | float32 | varh |  | R | O
Fixed Block |  | 124 | 122 | 2 | Evt | Events |  | bitfield32 |  |  | R | M | Meter Event Flags
bitfield32 | Evt |  |  | Name: M_EVENT_Power_Failure; Value: 2
bitfield32 | Evt |  |  | Name: M_EVENT_Under_Voltage; Value: 3
bitfield32 | Evt |  |  | Name: M_EVENT_Low_PF; Value: 4
bitfield32 | Evt |  |  | Name: M_EVENT_Over_Current; Value: 5
bitfield32 | Evt |  |  | Name: M_EVENT_Over_Voltage; Value: 6
bitfield32 | Evt |  |  | Name: M_EVENT_Missing_Sensor; Value: 7
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved1; Value: 8
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved2; Value: 9
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved3; Value: 10
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved4; Value: 11
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved5; Value: 12
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved6; Value: 13
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved7; Value: 14
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved8; Value: 15
bitfield32 | Evt |  |  | Name: M_EVENT_OEM01; Value: 16
bitfield32 | Evt |  |  | Name: M_EVENT_OEM02; Value: 17
bitfield32 | Evt |  |  | Name: M_EVENT_OEM03; Value: 18
bitfield32 | Evt |  |  | Name: M_EVENT_OEM04; Value: 19
bitfield32 | Evt |  |  | Name: M_EVENT_OEM05; Value: 20
bitfield32 | Evt |  |  | Name: M_EVENT_OEM06; Value: 21
bitfield32 | Evt |  |  | Name: M_EVENT_OEM07; Value: 22
bitfield32 | Evt |  |  | Name: M_EVENT_OEM08; Value: 23
bitfield32 | Evt |  |  | Name: M_EVENT_OEM09; Value: 24
bitfield32 | Evt |  |  | Name: M_EVENT_OEM10; Value: 25
bitfield32 | Evt |  |  | Name: M_EVENT_OEM11; Value: 26
bitfield32 | Evt |  |  | Name: M_EVENT_OEM12; Value: 27
bitfield32 | Evt |  |  | Name: M_EVENT_OEM13; Value: 28
bitfield32 | Evt |  |  | Name: M_EVENT_OEM14; Value: 29
bitfield32 | Evt |  |  | Name: M_EVENT_OEM15; Value: 30
bitfield32 | Evt |  |  | Label: Power Failure; Value: 30 |  | Loss of power or phase
bitfield32 | Evt |  |  | Label: Under Voltage; Value: 30 |  | Voltage below threshold (Phase Loss)
bitfield32 | Evt |  |  | Label: Low PF; Value: 30 |  | Power Factor below threshold
bitfield32 | Evt |  |  | Label: Over Current; Value: 30 |  | Current Input over threshold
bitfield32 | Evt |  |  | Label: Over Voltage; Value: 30 |  | Voltage Input over threshold
bitfield32 | Evt |  |  | Label: Missing Sensor; Value: 30 |  | Sensor not connected
bitfield32 | Evt |  |  | Label: OEM01; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM02; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM01; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM04; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM05; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM06; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM07; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM08; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM09; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM10; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM11; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM12; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM13; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM14; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM15; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM16; Value: 30 |  | Reserved for OEM use

## 212
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | split single phase (ABN) meter | 212 | uint16 |  |  | R | M |  | Float
Header |  | 1 |  | 1 | L |  | 124 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 2 | A | Amps |  | float32 | A |  | R | M | Total AC Current
Fixed Block |  | 4 | 2 | 2 | AphA | Amps PhaseA |  | float32 | A |  | R | M | Phase A Current
Fixed Block |  | 6 | 4 | 2 | AphB | Amps PhaseB |  | float32 | A |  | R | M | Phase B Current
Fixed Block |  | 8 | 6 | 2 | AphC | Amps PhaseC |  | float32 | A |  | R | O | Phase C Current
Fixed Block |  | 10 | 8 | 2 | PhV | Voltage LN |  | float32 | V |  | R | M | Line to Neutral AC Voltage (average of active phases)
Fixed Block |  | 12 | 10 | 2 | PhVphA | Phase Voltage AN |  | float32 | V |  | R | M | Phase Voltage AN
Fixed Block |  | 14 | 12 | 2 | PhVphB | Phase Voltage BN |  | float32 | V |  | R | M | Phase Voltage BN
Fixed Block |  | 16 | 14 | 2 | PhVphC | Phase Voltage CN |  | float32 | V |  | R | O | Phase Voltage CN
Fixed Block |  | 18 | 16 | 2 | PPV | Voltage LL |  | float32 | V |  | R | M | Line to Line AC Voltage (average of active phases)
Fixed Block |  | 20 | 18 | 2 | PPVphAB | Phase Voltage AB |  | float32 | V |  | R | M | Phase Voltage AB
Fixed Block |  | 22 | 20 | 2 | PPVphBC | Phase Voltage BC |  | float32 | V |  | R | O | Phase Voltage BC
Fixed Block |  | 24 | 22 | 2 | PPVphCA | Phase Voltage CA |  | float32 | V |  | R | O | Phase Voltage CA
Fixed Block |  | 26 | 24 | 2 | Hz | Hz |  | float32 | Hz |  | R | M | Frequency
Fixed Block |  | 28 | 26 | 2 | W | Watts |  | float32 | W |  | R | M | Total Real Power
Fixed Block |  | 30 | 28 | 2 | WphA | Watts phase A |  | float32 | W |  | R | O
Fixed Block |  | 32 | 30 | 2 | WphB | Watts phase B |  | float32 | W |  | R | O
Fixed Block |  | 34 | 32 | 2 | WphC | Watts phase C |  | float32 | W |  | R | O
Fixed Block |  | 36 | 34 | 2 | VA | VA |  | float32 | VA |  | R | O | AC Apparent Power
Fixed Block |  | 38 | 36 | 2 | VAphA | VA phase A |  | float32 | VA |  | R | O
Fixed Block |  | 40 | 38 | 2 | VAphB | VA phase B |  | float32 | VA |  | R | O
Fixed Block |  | 42 | 40 | 2 | VAphC | VA phase C |  | float32 | VA |  | R | O
Fixed Block |  | 44 | 42 | 2 | VAR | VAR |  | float32 | var |  | R | O | Reactive Power
Fixed Block |  | 46 | 44 | 2 | VARphA | VAR phase A |  | float32 | var |  | R | O
Fixed Block |  | 48 | 46 | 2 | VARphB | VAR phase B |  | float32 | var |  | R | O
Fixed Block |  | 50 | 48 | 2 | VARphC | VAR phase C |  | float32 | var |  | R | O
Fixed Block |  | 52 | 50 | 2 | PF | PF |  | float32 | PF |  | R | O | Power Factor
Fixed Block |  | 54 | 52 | 2 | PFphA | PF phase A |  | float32 | PF |  | R | O
Fixed Block |  | 56 | 54 | 2 | PFphB | PF phase B |  | float32 | PF |  | R | O
Fixed Block |  | 58 | 56 | 2 | PFphC | PF phase C |  | float32 | PF |  | R | O
Fixed Block |  | 60 | 58 | 2 | TotWhExp | Total Watt-hours Exported |  | float32 | Wh |  | R | M | Total Real Energy Exported
Fixed Block |  | 62 | 60 | 2 | TotWhExpPhA | Total Watt-hours Exported phase A |  | float32 | Wh |  | R | O
Fixed Block |  | 64 | 62 | 2 | TotWhExpPhB | Total Watt-hours Exported phase B |  | float32 | Wh |  | R | O
Fixed Block |  | 66 | 64 | 2 | TotWhExpPhC | Total Watt-hours Exported phase C |  | float32 | Wh |  | R | O
Fixed Block |  | 68 | 66 | 2 | TotWhImp | Total Watt-hours Imported |  | float32 | Wh |  | R | M | Total Real Energy Imported
Fixed Block |  | 70 | 68 | 2 | TotWhImpPhA | Total Watt-hours Imported phase A |  | float32 | Wh |  | R | O
Fixed Block |  | 72 | 70 | 2 | TotWhImpPhB | Total Watt-hours Imported phase B |  | float32 | Wh |  | R | O
Fixed Block |  | 74 | 72 | 2 | TotWhImpPhC | Total Watt-hours Imported phase C |  | float32 | Wh |  | R | O
Fixed Block |  | 76 | 74 | 2 | TotVAhExp | Total VA-hours Exported |  | float32 | VAh |  | R | O | Total Apparent Energy Exported
Fixed Block |  | 78 | 76 | 2 | TotVAhExpPhA | Total VA-hours Exported phase A |  | float32 | VAh |  | R | O
Fixed Block |  | 80 | 78 | 2 | TotVAhExpPhB | Total VA-hours Exported phase B |  | float32 | VAh |  | R | O
Fixed Block |  | 82 | 80 | 2 | TotVAhExpPhC | Total VA-hours Exported phase C |  | float32 | VAh |  | R | O
Fixed Block |  | 84 | 82 | 2 | TotVAhImp | Total VA-hours Imported |  | float32 | VAh |  | R | O | Total Apparent Energy Imported
Fixed Block |  | 86 | 84 | 2 | TotVAhImpPhA | Total VA-hours Imported phase A |  | float32 | VAh |  | R | O
Fixed Block |  | 88 | 86 | 2 | TotVAhImpPhB | Total VA-hours Imported phase B |  | float32 | VAh |  | R | O
Fixed Block |  | 90 | 88 | 2 | TotVAhImpPhC | Total VA-hours Imported phase C |  | float32 | VAh |  | R | O
Fixed Block |  | 92 | 90 | 2 | TotVArhImpQ1 | Total VAR-hours Imported Q1 |  | float32 | varh |  | R | O | Total Reactive Energy Imported Quadrant 1
Fixed Block |  | 94 | 92 | 2 | TotVArhImpQ1phA |  |  | float32 | varh |  | R | O
Fixed Block |  | 96 | 94 | 2 | TotVArhImpQ1phB |  |  | float32 | varh |  | R | O
Fixed Block |  | 98 | 96 | 2 | TotVArhImpQ1phC |  |  | float32 | varh |  | R | O
Fixed Block |  | 100 | 98 | 2 | TotVArhImpQ2 | Total VAr-hours Imported Q2 |  | float32 | varh |  | R | O | Total Reactive Power Imported Quadrant 2
Fixed Block |  | 102 | 100 | 2 | TotVArhImpQ2phA |  |  | float32 | varh |  | R | O
Fixed Block |  | 104 | 102 | 2 | TotVArhImpQ2phB |  |  | float32 | varh |  | R | O
Fixed Block |  | 106 | 104 | 2 | TotVArhImpQ2phC |  |  | float32 | varh |  | R | O
Fixed Block |  | 108 | 106 | 2 | TotVArhExpQ3 | Total VAr-hours Exported Q3 |  | float32 | varh |  | R | O | Total Reactive Power Exported Quadrant 3
Fixed Block |  | 110 | 108 | 2 | TotVArhExpQ3phA |  |  | float32 | varh |  | R | O
Fixed Block |  | 112 | 110 | 2 | TotVArhExpQ3phB |  |  | float32 | varh |  | R | O
Fixed Block |  | 114 | 112 | 2 | TotVArhExpQ3phC |  |  | float32 | varh |  | R | O
Fixed Block |  | 116 | 114 | 2 | TotVArhExpQ4 | Total VAr-hours Exported Q4 |  | float32 | varh |  | R | O | Total Reactive Power Exported Quadrant 4
Fixed Block |  | 118 | 116 | 2 | TotVArhExpQ4phA |  |  | float32 | varh |  | R | O
Fixed Block |  | 120 | 118 | 2 | TotVArhExpQ4phB |  |  | float32 | varh |  | R | O
Fixed Block |  | 122 | 120 | 2 | TotVArhExpQ4phC |  |  | float32 | varh |  | R | O
Fixed Block |  | 124 | 122 | 2 | Evt | Events |  | bitfield32 |  |  | R | M | Meter Event Flags
bitfield32 | Evt |  |  | Name: M_EVENT_Power_Failure; Value: 2
bitfield32 | Evt |  |  | Name: M_EVENT_Under_Voltage; Value: 3
bitfield32 | Evt |  |  | Name: M_EVENT_Low_PF; Value: 4
bitfield32 | Evt |  |  | Name: M_EVENT_Over_Current; Value: 5
bitfield32 | Evt |  |  | Name: M_EVENT_Over_Voltage; Value: 6
bitfield32 | Evt |  |  | Name: M_EVENT_Missing_Sensor; Value: 7
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved1; Value: 8
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved2; Value: 9
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved3; Value: 10
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved4; Value: 11
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved5; Value: 12
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved6; Value: 13
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved7; Value: 14
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved8; Value: 15
bitfield32 | Evt |  |  | Name: M_EVENT_OEM01; Value: 16
bitfield32 | Evt |  |  | Name: M_EVENT_OEM02; Value: 17
bitfield32 | Evt |  |  | Name: M_EVENT_OEM03; Value: 18
bitfield32 | Evt |  |  | Name: M_EVENT_OEM04; Value: 19
bitfield32 | Evt |  |  | Name: M_EVENT_OEM05; Value: 20
bitfield32 | Evt |  |  | Name: M_EVENT_OEM06; Value: 21
bitfield32 | Evt |  |  | Name: M_EVENT_OEM07; Value: 22
bitfield32 | Evt |  |  | Name: M_EVENT_OEM08; Value: 23
bitfield32 | Evt |  |  | Name: M_EVENT_OEM09; Value: 24
bitfield32 | Evt |  |  | Name: M_EVENT_OEM10; Value: 25
bitfield32 | Evt |  |  | Name: M_EVENT_OEM11; Value: 26
bitfield32 | Evt |  |  | Name: M_EVENT_OEM12; Value: 27
bitfield32 | Evt |  |  | Name: M_EVENT_OEM13; Value: 28
bitfield32 | Evt |  |  | Name: M_EVENT_OEM14; Value: 29
bitfield32 | Evt |  |  | Name: M_EVENT_OEM15; Value: 30
bitfield32 | Evt |  |  | Label: Power Failure; Value: 30 |  | Loss of power or phase
bitfield32 | Evt |  |  | Label: Under Voltage; Value: 30 |  | Voltage below threshold (Phase Loss)
bitfield32 | Evt |  |  | Label: Low PF; Value: 30 |  | Power Factor below threshold
bitfield32 | Evt |  |  | Label: Over Current; Value: 30 |  | Current Input over threshold
bitfield32 | Evt |  |  | Label: Over Voltage; Value: 30 |  | Voltage Input over threshold
bitfield32 | Evt |  |  | Label: Missing Sensor; Value: 30 |  | Sensor not connected
bitfield32 | Evt |  |  | Label: OEM01; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM02; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM01; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM04; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM05; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM06; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM07; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM08; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM09; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM10; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM11; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM12; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM13; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM14; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM15; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM16; Value: 30 |  | Reserved for OEM use

## 213
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | wye-connect three phase (abcn) meter | 213 | uint16 |  |  | R | M |  | Float
Header |  | 1 |  | 1 | L |  | 124 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 2 | A | Amps |  | float32 | A |  | R | M | Total AC Current
Fixed Block |  | 4 | 2 | 2 | AphA | Amps PhaseA |  | float32 | A |  | R | M | Phase A Current
Fixed Block |  | 6 | 4 | 2 | AphB | Amps PhaseB |  | float32 | A |  | R | M | Phase B Current
Fixed Block |  | 8 | 6 | 2 | AphC | Amps PhaseC |  | float32 | A |  | R | M | Phase C Current
Fixed Block |  | 10 | 8 | 2 | PhV | Voltage LN |  | float32 | V |  | R | M | Line to Neutral AC Voltage (average of active phases)
Fixed Block |  | 12 | 10 | 2 | PhVphA | Phase Voltage AN |  | float32 | V |  | R | M | Phase Voltage AN
Fixed Block |  | 14 | 12 | 2 | PhVphB | Phase Voltage BN |  | float32 | V |  | R | M | Phase Voltage BN
Fixed Block |  | 16 | 14 | 2 | PhVphC | Phase Voltage CN |  | float32 | V |  | R | M | Phase Voltage CN
Fixed Block |  | 18 | 16 | 2 | PPV | Voltage LL |  | float32 | V |  | R | M | Line to Line AC Voltage (average of active phases)
Fixed Block |  | 20 | 18 | 2 | PPVphAB | Phase Voltage AB |  | float32 | V |  | R | M | Phase Voltage AB
Fixed Block |  | 22 | 20 | 2 | PPVphBC | Phase Voltage BC |  | float32 | V |  | R | M | Phase Voltage BC
Fixed Block |  | 24 | 22 | 2 | PPVphCA | Phase Voltage CA |  | float32 | V |  | R | M | Phase Voltage CA
Fixed Block |  | 26 | 24 | 2 | Hz | Hz |  | float32 | Hz |  | R | M | Frequency
Fixed Block |  | 28 | 26 | 2 | W | Watts |  | float32 | W |  | R | M | Total Real Power
Fixed Block |  | 30 | 28 | 2 | WphA | Watts phase A |  | float32 | W |  | R | O
Fixed Block |  | 32 | 30 | 2 | WphB | Watts phase B |  | float32 | W |  | R | O
Fixed Block |  | 34 | 32 | 2 | WphC | Watts phase C |  | float32 | W |  | R | O
Fixed Block |  | 36 | 34 | 2 | VA | VA |  | float32 | VA |  | R | O | AC Apparent Power
Fixed Block |  | 38 | 36 | 2 | VAphA | VA phase A |  | float32 | VA |  | R | O
Fixed Block |  | 40 | 38 | 2 | VAphB | VA phase B |  | float32 | VA |  | R | O
Fixed Block |  | 42 | 40 | 2 | VAphC | VA phase C |  | float32 | VA |  | R | O
Fixed Block |  | 44 | 42 | 2 | VAR | VAR |  | float32 | var |  | R | O | Reactive Power
Fixed Block |  | 46 | 44 | 2 | VARphA | VAR phase A |  | float32 | var |  | R | O
Fixed Block |  | 48 | 46 | 2 | VARphB | VAR phase B |  | float32 | var |  | R | O
Fixed Block |  | 50 | 48 | 2 | VARphC | VAR phase C |  | float32 | var |  | R | O
Fixed Block |  | 52 | 50 | 2 | PF | PF |  | float32 | PF |  | R | O | Power Factor
Fixed Block |  | 54 | 52 | 2 | PFphA | PF phase A |  | float32 | PF |  | R | O
Fixed Block |  | 56 | 54 | 2 | PFphB | PF phase B |  | float32 | PF |  | R | O
Fixed Block |  | 58 | 56 | 2 | PFphC | PF phase C |  | float32 | PF |  | R | O
Fixed Block |  | 60 | 58 | 2 | TotWhExp | Total Watt-hours Exported |  | float32 | Wh |  | R | M | Total Real Energy Exported
Fixed Block |  | 62 | 60 | 2 | TotWhExpPhA | Total Watt-hours Exported phase A |  | float32 | Wh |  | R | O
Fixed Block |  | 64 | 62 | 2 | TotWhExpPhB | Total Watt-hours Exported phase B |  | float32 | Wh |  | R | O
Fixed Block |  | 66 | 64 | 2 | TotWhExpPhC | Total Watt-hours Exported phase C |  | float32 | Wh |  | R | O
Fixed Block |  | 68 | 66 | 2 | TotWhImp | Total Watt-hours Imported |  | float32 | Wh |  | R | M | Total Real Energy Imported
Fixed Block |  | 70 | 68 | 2 | TotWhImpPhA | Total Watt-hours Imported phase A |  | float32 | Wh |  | R | O
Fixed Block |  | 72 | 70 | 2 | TotWhImpPhB | Total Watt-hours Imported phase B |  | float32 | Wh |  | R | O
Fixed Block |  | 74 | 72 | 2 | TotWhImpPhC | Total Watt-hours Imported phase C |  | float32 | Wh |  | R | O
Fixed Block |  | 76 | 74 | 2 | TotVAhExp | Total VA-hours Exported |  | float32 | VAh |  | R | O | Total Apparent Energy Exported
Fixed Block |  | 78 | 76 | 2 | TotVAhExpPhA | Total VA-hours Exported phase A |  | float32 | VAh |  | R | O
Fixed Block |  | 80 | 78 | 2 | TotVAhExpPhB | Total VA-hours Exported phase B |  | float32 | VAh |  | R | O
Fixed Block |  | 82 | 80 | 2 | TotVAhExpPhC | Total VA-hours Exported phase C |  | float32 | VAh |  | R | O
Fixed Block |  | 84 | 82 | 2 | TotVAhImp | Total VA-hours Imported |  | float32 | VAh |  | R | O | Total Apparent Energy Imported
Fixed Block |  | 86 | 84 | 2 | TotVAhImpPhA | Total VA-hours Imported phase A |  | float32 | VAh |  | R | O
Fixed Block |  | 88 | 86 | 2 | TotVAhImpPhB | Total VA-hours Imported phase B |  | float32 | VAh |  | R | O
Fixed Block |  | 90 | 88 | 2 | TotVAhImpPhC | Total VA-hours Imported phase C |  | float32 | VAh |  | R | O
Fixed Block |  | 92 | 90 | 2 | TotVArhImpQ1 | Total VAR-hours Imported Q1 |  | float32 | varh |  | R | O | Total Reactive Energy Imported Quadrant 1
Fixed Block |  | 94 | 92 | 2 | TotVArhImpQ1phA |  |  | float32 | varh |  | R | O
Fixed Block |  | 96 | 94 | 2 | TotVArhImpQ1phB |  |  | float32 | varh |  | R | O
Fixed Block |  | 98 | 96 | 2 | TotVArhImpQ1phC |  |  | float32 | varh |  | R | O
Fixed Block |  | 100 | 98 | 2 | TotVArhImpQ2 | Total VAr-hours Imported Q2 |  | float32 | varh |  | R | O | Total Reactive Power Imported Quadrant 2
Fixed Block |  | 102 | 100 | 2 | TotVArhImpQ2phA |  |  | float32 | varh |  | R | O
Fixed Block |  | 104 | 102 | 2 | TotVArhImpQ2phB |  |  | float32 | varh |  | R | O
Fixed Block |  | 106 | 104 | 2 | TotVArhImpQ2phC |  |  | float32 | varh |  | R | O
Fixed Block |  | 108 | 106 | 2 | TotVArhExpQ3 | Total VAr-hours Exported Q3 |  | float32 | varh |  | R | O | Total Reactive Power Exported Quadrant 3
Fixed Block |  | 110 | 108 | 2 | TotVArhExpQ3phA |  |  | float32 | varh |  | R | O
Fixed Block |  | 112 | 110 | 2 | TotVArhExpQ3phB |  |  | float32 | varh |  | R | O
Fixed Block |  | 114 | 112 | 2 | TotVArhExpQ3phC |  |  | float32 | varh |  | R | O
Fixed Block |  | 116 | 114 | 2 | TotVArhExpQ4 | Total VAr-hours Exported Q4 |  | float32 | varh |  | R | O | Total Reactive Power Exported Quadrant 4
Fixed Block |  | 118 | 116 | 2 | TotVArhExpQ4phA |  |  | float32 | varh |  | R | O
Fixed Block |  | 120 | 118 | 2 | TotVArhExpQ4phB |  |  | float32 | varh |  | R | O
Fixed Block |  | 122 | 120 | 2 | TotVArhExpQ4phC |  |  | float32 | varh |  | R | O
Fixed Block |  | 124 | 122 | 2 | Evt | Events |  | bitfield32 |  |  | R | M | Meter Event Flags
bitfield32 | Evt |  |  | Name: M_EVENT_Power_Failure; Value: 2
bitfield32 | Evt |  |  | Name: M_EVENT_Under_Voltage; Value: 3
bitfield32 | Evt |  |  | Name: M_EVENT_Low_PF; Value: 4
bitfield32 | Evt |  |  | Name: M_EVENT_Over_Current; Value: 5
bitfield32 | Evt |  |  | Name: M_EVENT_Over_Voltage; Value: 6
bitfield32 | Evt |  |  | Name: M_EVENT_Missing_Sensor; Value: 7
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved1; Value: 8
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved2; Value: 9
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved3; Value: 10
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved4; Value: 11
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved5; Value: 12
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved6; Value: 13
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved7; Value: 14
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved8; Value: 15
bitfield32 | Evt |  |  | Name: M_EVENT_OEM01; Value: 16
bitfield32 | Evt |  |  | Name: M_EVENT_OEM02; Value: 17
bitfield32 | Evt |  |  | Name: M_EVENT_OEM03; Value: 18
bitfield32 | Evt |  |  | Name: M_EVENT_OEM04; Value: 19
bitfield32 | Evt |  |  | Name: M_EVENT_OEM05; Value: 20
bitfield32 | Evt |  |  | Name: M_EVENT_OEM06; Value: 21
bitfield32 | Evt |  |  | Name: M_EVENT_OEM07; Value: 22
bitfield32 | Evt |  |  | Name: M_EVENT_OEM08; Value: 23
bitfield32 | Evt |  |  | Name: M_EVENT_OEM09; Value: 24
bitfield32 | Evt |  |  | Name: M_EVENT_OEM10; Value: 25
bitfield32 | Evt |  |  | Name: M_EVENT_OEM11; Value: 26
bitfield32 | Evt |  |  | Name: M_EVENT_OEM12; Value: 27
bitfield32 | Evt |  |  | Name: M_EVENT_OEM13; Value: 28
bitfield32 | Evt |  |  | Name: M_EVENT_OEM14; Value: 29
bitfield32 | Evt |  |  | Name: M_EVENT_OEM15; Value: 30
bitfield32 | Evt |  |  | Label: Power Failure; Value: 30 |  | Loss of power or phase
bitfield32 | Evt |  |  | Label: Under Voltage; Value: 30 |  | Voltage below threshold (Phase Loss)
bitfield32 | Evt |  |  | Label: Low PF; Value: 30 |  | Power Factor below threshold
bitfield32 | Evt |  |  | Label: Over Current; Value: 30 |  | Current Input over threshold
bitfield32 | Evt |  |  | Label: Over Voltage; Value: 30 |  | Voltage Input over threshold
bitfield32 | Evt |  |  | Label: Missing Sensor; Value: 30 |  | Sensor not connected
bitfield32 | Evt |  |  | Label: OEM01; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM02; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM01; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM04; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM05; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM06; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM07; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM08; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM09; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM10; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM11; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM12; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM13; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM14; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM15; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM16; Value: 30 |  | Reserved for OEM use

## 214
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | delta-connect three phase (abc) meter | 214 | uint16 |  |  | R | M |  | Float
Header |  | 1 |  | 1 | L |  | 124 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 2 | A | Amps |  | float32 | A |  | R | M | Total AC Current
Fixed Block |  | 4 | 2 | 2 | AphA | Amps PhaseA |  | float32 | A |  | R | M | Phase A Current
Fixed Block |  | 6 | 4 | 2 | AphB | Amps PhaseB |  | float32 | A |  | R | M | Phase B Current
Fixed Block |  | 8 | 6 | 2 | AphC | Amps PhaseC |  | float32 | A |  | R | M | Phase C Current
Fixed Block |  | 10 | 8 | 2 | PhV | Voltage LN |  | float32 | V |  | R | O | Line to Neutral AC Voltage (average of active phases)
Fixed Block |  | 12 | 10 | 2 | PhVphA | Phase Voltage AN |  | float32 | V |  | R | O | Phase Voltage AN
Fixed Block |  | 14 | 12 | 2 | PhVphB | Phase Voltage BN |  | float32 | V |  | R | O | Phase Voltage BN
Fixed Block |  | 16 | 14 | 2 | PhVphC | Phase Voltage CN |  | float32 | V |  | R | O | Phase Voltage CN
Fixed Block |  | 18 | 16 | 2 | PPV | Voltage LL |  | float32 | V |  | R | M | Line to Line AC Voltage (average of active phases)
Fixed Block |  | 20 | 18 | 2 | PPVphAB | Phase Voltage AB |  | float32 | V |  | R | M | Phase Voltage AB
Fixed Block |  | 22 | 20 | 2 | PPVphBC | Phase Voltage BC |  | float32 | V |  | R | M | Phase Voltage BC
Fixed Block |  | 24 | 22 | 2 | PPVphCA | Phase Voltage CA |  | float32 | V |  | R | M | Phase Voltage CA
Fixed Block |  | 26 | 24 | 2 | Hz | Hz |  | float32 | Hz |  | R | M | Frequency
Fixed Block |  | 28 | 26 | 2 | W | Watts |  | float32 | W |  | R | M | Total Real Power
Fixed Block |  | 30 | 28 | 2 | WphA | Watts phase A |  | float32 | W |  | R | O
Fixed Block |  | 32 | 30 | 2 | WphB | Watts phase B |  | float32 | W |  | R | O
Fixed Block |  | 34 | 32 | 2 | WphC | Watts phase C |  | float32 | W |  | R | O
Fixed Block |  | 36 | 34 | 2 | VA | VA |  | float32 | VA |  | R | O | AC Apparent Power
Fixed Block |  | 38 | 36 | 2 | VAphA | VA phase A |  | float32 | VA |  | R | O
Fixed Block |  | 40 | 38 | 2 | VAphB | VA phase B |  | float32 | VA |  | R | O
Fixed Block |  | 42 | 40 | 2 | VAphC | VA phase C |  | float32 | VA |  | R | O
Fixed Block |  | 44 | 42 | 2 | VAR | VAR |  | float32 | var |  | R | O | Reactive Power
Fixed Block |  | 46 | 44 | 2 | VARphA | VAR phase A |  | float32 | var |  | R | O
Fixed Block |  | 48 | 46 | 2 | VARphB | VAR phase B |  | float32 | var |  | R | O
Fixed Block |  | 50 | 48 | 2 | VARphC | VAR phase C |  | float32 | var |  | R | O
Fixed Block |  | 52 | 50 | 2 | PF | PF |  | float32 | PF |  | R | O | Power Factor
Fixed Block |  | 54 | 52 | 2 | PFphA | PF phase A |  | float32 | PF |  | R | O
Fixed Block |  | 56 | 54 | 2 | PFphB | PF phase B |  | float32 | PF |  | R | O
Fixed Block |  | 58 | 56 | 2 | PFphC | PF phase C |  | float32 | PF |  | R | O
Fixed Block |  | 60 | 58 | 2 | TotWhExp | Total Watt-hours Exported |  | float32 | Wh |  | R | M | Total Real Energy Exported
Fixed Block |  | 62 | 60 | 2 | TotWhExpPhA | Total Watt-hours Exported phase A |  | float32 | Wh |  | R | O
Fixed Block |  | 64 | 62 | 2 | TotWhExpPhB | Total Watt-hours Exported phase B |  | float32 | Wh |  | R | O
Fixed Block |  | 66 | 64 | 2 | TotWhExpPhC | Total Watt-hours Exported phase C |  | float32 | Wh |  | R | O
Fixed Block |  | 68 | 66 | 2 | TotWhImp | Total Watt-hours Imported |  | float32 | Wh |  | R | M | Total Real Energy Imported
Fixed Block |  | 70 | 68 | 2 | TotWhImpPhA | Total Watt-hours Imported phase A |  | float32 | Wh |  | R | O
Fixed Block |  | 72 | 70 | 2 | TotWhImpPhB | Total Watt-hours Imported phase B |  | float32 | Wh |  | R | O
Fixed Block |  | 74 | 72 | 2 | TotWhImpPhC | Total Watt-hours Imported phase C |  | float32 | Wh |  | R | O
Fixed Block |  | 76 | 74 | 2 | TotVAhExp | Total VA-hours Exported |  | float32 | VAh |  | R | O | Total Apparent Energy Exported
Fixed Block |  | 78 | 76 | 2 | TotVAhExpPhA | Total VA-hours Exported phase A |  | float32 | VAh |  | R | O
Fixed Block |  | 80 | 78 | 2 | TotVAhExpPhB | Total VA-hours Exported phase B |  | float32 | VAh |  | R | O
Fixed Block |  | 82 | 80 | 2 | TotVAhExpPhC | Total VA-hours Exported phase C |  | float32 | VAh |  | R | O
Fixed Block |  | 84 | 82 | 2 | TotVAhImp | Total VA-hours Imported |  | float32 | VAh |  | R | O | Total Apparent Energy Imported
Fixed Block |  | 86 | 84 | 2 | TotVAhImpPhA | Total VA-hours Imported phase A |  | float32 | VAh |  | R | O
Fixed Block |  | 88 | 86 | 2 | TotVAhImpPhB | Total VA-hours Imported phase B |  | float32 | VAh |  | R | O
Fixed Block |  | 90 | 88 | 2 | TotVAhImpPhC | Total VA-hours Imported phase C |  | float32 | VAh |  | R | O
Fixed Block |  | 92 | 90 | 2 | TotVArhImpQ1 | Total VAR-hours Imported Q1 |  | float32 | varh |  | R | O | Total Reactive Energy Imported Quadrant 1
Fixed Block |  | 94 | 92 | 2 | TotVArhImpQ1phA |  |  | float32 | varh |  | R | O
Fixed Block |  | 96 | 94 | 2 | TotVArhImpQ1phB |  |  | float32 | varh |  | R | O
Fixed Block |  | 98 | 96 | 2 | TotVArhImpQ1phC |  |  | float32 | varh |  | R | O
Fixed Block |  | 100 | 98 | 2 | TotVArhImpQ2 | Total VAr-hours Imported Q2 |  | float32 | varh |  | R | O | Total Reactive Power Imported Quadrant 2
Fixed Block |  | 102 | 100 | 2 | TotVArhImpQ2phA |  |  | float32 | varh |  | R | O
Fixed Block |  | 104 | 102 | 2 | TotVArhImpQ2phB |  |  | float32 | varh |  | R | O
Fixed Block |  | 106 | 104 | 2 | TotVArhImpQ2phC |  |  | float32 | varh |  | R | O
Fixed Block |  | 108 | 106 | 2 | TotVArhExpQ3 | Total VAr-hours Exported Q3 |  | float32 | varh |  | R | O | Total Reactive Power Exported Quadrant 3
Fixed Block |  | 110 | 108 | 2 | TotVArhExpQ3phA |  |  | float32 | varh |  | R | O
Fixed Block |  | 112 | 110 | 2 | TotVArhExpQ3phB |  |  | float32 | varh |  | R | O
Fixed Block |  | 114 | 112 | 2 | TotVArhExpQ3phC |  |  | float32 | varh |  | R | O
Fixed Block |  | 116 | 114 | 2 | TotVArhExpQ4 | Total VAr-hours Exported Q4 |  | float32 | varh |  | R | O | Total Reactive Power Exported Quadrant 4
Fixed Block |  | 118 | 116 | 2 | TotVArhExpQ4phA |  |  | float32 | varh |  | R | O
Fixed Block |  | 120 | 118 | 2 | TotVArhExpQ4phB |  |  | float32 | varh |  | R | O
Fixed Block |  | 122 | 120 | 2 | TotVArhExpQ4phC |  |  | float32 | varh |  | R | O
Fixed Block |  | 124 | 122 | 2 | Evt | Events |  | bitfield32 |  |  | R | M | Meter Event Flags
bitfield32 | Evt |  |  | Name: M_EVENT_Power_Failure; Value: 2
bitfield32 | Evt |  |  | Name: M_EVENT_Under_Voltage; Value: 3
bitfield32 | Evt |  |  | Name: M_EVENT_Low_PF; Value: 4
bitfield32 | Evt |  |  | Name: M_EVENT_Over_Current; Value: 5
bitfield32 | Evt |  |  | Name: M_EVENT_Over_Voltage; Value: 6
bitfield32 | Evt |  |  | Name: M_EVENT_Missing_Sensor; Value: 7
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved1; Value: 8
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved2; Value: 9
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved3; Value: 10
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved4; Value: 11
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved5; Value: 12
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved6; Value: 13
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved7; Value: 14
bitfield32 | Evt |  |  | Name: M_EVENT_Reserved8; Value: 15
bitfield32 | Evt |  |  | Name: M_EVENT_OEM01; Value: 16
bitfield32 | Evt |  |  | Name: M_EVENT_OEM02; Value: 17
bitfield32 | Evt |  |  | Name: M_EVENT_OEM03; Value: 18
bitfield32 | Evt |  |  | Name: M_EVENT_OEM04; Value: 19
bitfield32 | Evt |  |  | Name: M_EVENT_OEM05; Value: 20
bitfield32 | Evt |  |  | Name: M_EVENT_OEM06; Value: 21
bitfield32 | Evt |  |  | Name: M_EVENT_OEM07; Value: 22
bitfield32 | Evt |  |  | Name: M_EVENT_OEM08; Value: 23
bitfield32 | Evt |  |  | Name: M_EVENT_OEM09; Value: 24
bitfield32 | Evt |  |  | Name: M_EVENT_OEM10; Value: 25
bitfield32 | Evt |  |  | Name: M_EVENT_OEM11; Value: 26
bitfield32 | Evt |  |  | Name: M_EVENT_OEM12; Value: 27
bitfield32 | Evt |  |  | Name: M_EVENT_OEM13; Value: 28
bitfield32 | Evt |  |  | Name: M_EVENT_OEM14; Value: 29
bitfield32 | Evt |  |  | Name: M_EVENT_OEM15; Value: 30
bitfield32 | Evt |  |  | Label: Power Failure; Value: 30 |  | Loss of power or phase
bitfield32 | Evt |  |  | Label: Under Voltage; Value: 30 |  | Voltage below threshold (Phase Loss)
bitfield32 | Evt |  |  | Label: Low PF; Value: 30 |  | Power Factor below threshold
bitfield32 | Evt |  |  | Label: Over Current; Value: 30 |  | Current Input over threshold
bitfield32 | Evt |  |  | Label: Over Voltage; Value: 30 |  | Voltage Input over threshold
bitfield32 | Evt |  |  | Label: Missing Sensor; Value: 30 |  | Sensor not connected
bitfield32 | Evt |  |  | Label: OEM01; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM02; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM01; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM04; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM05; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM06; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM07; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM08; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM09; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM10; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM11; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM12; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM13; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM14; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM15; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM16; Value: 30 |  | Reserved for OEM use

## 220
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Secure AC Meter Selected Readings | 220 | uint16 |  |  | R | M | Include this model for secure metering
Header |  | 1 |  | 1 | L |  | 42 + (RB Count * 1) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | A | Amps |  | int16 | A | A_SF | R | M | Total AC Current
Fixed Block |  | 3 | 1 | Size: 1; Name: A_SF; Type: sunssf; R/W: R | M | Current scale factor
Fixed Block |  | 4 | 2 | 1 | PhV | Voltage |  | int16 | V | V_SF | R | O | Average phase or line voltage
Fixed Block |  | 5 | 3 | Size: 1; Name: V_SF; Type: sunssf; R/W: R | M | Voltage scale factor
Fixed Block |  | 6 | 4 | 1 | Hz | Hz |  | int16 | Hz | Hz_SF | R | M | Frequency
Fixed Block |  | 7 | 5 | Size: 1; Name: Hz_SF; Type: sunssf; R/W: R | O | Frequency scale factor
Fixed Block |  | 8 | 6 | 1 | W | Watts |  | int16 | W | W_SF | R | M | Total Real Power
Fixed Block |  | 9 | 7 | Size: 1; Name: W_SF; Type: sunssf; R/W: R | M | Real Power scale factor
Fixed Block |  | 10 | 8 | 1 | VA | VA |  | int16 | VA | VA_SF | R | O | AC Apparent Power
Fixed Block |  | 11 | 9 | Size: 1; Name: VA_SF; Type: sunssf; R/W: R | O | Apparent Power scale factor
Fixed Block |  | 12 | 10 | 1 | VAR | VAR |  | int16 | var | VAR_SF | R | O | Reactive Power
Fixed Block |  | 13 | 11 | Size: 1; Name: VAR_SF; Type: sunssf; R/W: R | O | Reactive Power scale factor
Fixed Block |  | 14 | 12 | 1 | PF | PF |  | int16 | Pct | PF_SF | R | O | Power Factor
Fixed Block |  | 15 | 13 | Size: 1; Name: PF_SF; Type: sunssf; R/W: R | O | Power Factor scale factor
Fixed Block |  | 16 | 14 | 2 | TotWhExp | Total Watt-hours Exported |  | acc32 | Wh | TotWh_SF | R | M | Total Real Energy Exported
Fixed Block |  | 18 | 16 | 2 | TotWhImp | Total Watt-hours Imported |  | acc32 | Wh | TotWh_SF | R | M | Total Real Energy Imported
Fixed Block |  | 20 | 18 | Size: 1; Name: TotWh_SF; Type: sunssf; R/W: R | M | Real Energy scale factor
Fixed Block |  | 21 | 19 | 2 | TotVAhExp | Total VA-hours Exported |  | acc32 | VAh | TotVAh_SF | R | O | Total Apparent Energy Exported
Fixed Block |  | 23 | 21 | 2 | TotVAhImp | Total VA-hours Imported |  | acc32 | VAh | TotVAh_SF | R | O | Total Apparent Energy Imported
Fixed Block |  | 25 | 23 | Size: 1; Name: TotVAh_SF; Type: sunssf; R/W: R | O | Apparent Energy scale factor
Fixed Block |  | 26 | 24 | 2 | TotVArhImpQ1 | Total VAR-hours Imported Q1 |  | acc32 | varh | TotVArh_SF | R | O | Total Reactive Energy Imported Quadrant 1
Fixed Block |  | 28 | 26 | 2 | TotVArhImpQ2 | Total VAr-hours Imported Q2 |  | acc32 | varh | TotVArh_SF | R | O | Total Reactive Power Imported Quadrant 2
Fixed Block |  | 30 | 28 | 2 | TotVArhExpQ3 | Total VAr-hours Exported Q3 |  | acc32 | varh | TotVArh_SF | R | O | Total Reactive Power Exported Quadrant 3
Fixed Block |  | 32 | 30 | 2 | TotVArhExpQ4 | Total VAr-hours Exported Q4 |  | acc32 | varh | TotVArh_SF | R | O | Total Reactive Power Exported Quadrant 4
Fixed Block |  | 34 | 32 | Size: 1; Name: TotVArh_SF; Type: sunssf; R/W: R | O | Reactive Energy scale factor
Fixed Block |  | 35 | 33 | 2 | Evt | Events |  | bitfield32 |  |  | R | M | Meter Event Flags
Fixed Block |  | 37 | 35 | Size: 1; Name: Rsrvd; Type: pad; R/W: R | M
Fixed Block |  | 38 | 36 | 2 | Ts | Timestamp |  | uint32 |  |  | R | M | Timestamp value is the number of seconds since January 1, 2000
Fixed Block |  | 40 | 38 | 1 | Ms | Milliseconds |  | uint16 |  |  | R | M | Millisecond counter 0-999
Fixed Block |  | 41 | 39 | 1 | Seq | Sequence |  | uint16 |  |  | R | M | Sequence number of request | Shall be advanced for each request
Fixed Block |  | 42 | 40 | 1 | Alg | Algorithm |  | enum16 |  |  | R | M | Algorithm used to compute the digital signature | For future proof
Fixed Block |  | 43 | 41 | 1 | N | N |  | uint16 |  |  | R | M | Number of registers comprising the digital signature. | The value of N must be at least 4 (64 bits)
Repeating Block |  | 44 | 0 | Size: 1; Name: DS; Type: uint16; R/W: R | M
bitfield32 | Evt |  |  | Name: Power_Failure; Label: Power Failure; Value: 2 |  | Loss of power or phase
bitfield32 | Evt |  |  | Name: Under_Voltage; Label: Under Voltage; Value: 3 |  | Voltage below threshold (Phase Loss)
bitfield32 | Evt |  |  | Name: Low_PF; Label: Low PF; Value: 4 |  | Power Factor below threshold
bitfield32 | Evt |  |  | Name: Over_Current; Label: Over Current; Value: 5 |  | Current Input over threshold
bitfield32 | Evt |  |  | Name: Over_Voltage; Label: Over Voltage; Value: 6 |  | Voltage Input over threshold
bitfield32 | Evt |  |  | Name: Missing_Sensor; Label: Missing Sensor; Value: 7 |  | Sensor not connected
bitfield32 | Evt |  |  | Name: OEM01; Label: OEM01; Value: 16 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Name: OEM02; Label: OEM02; Value: 17 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Name: OEM03; Label: OEM01; Value: 18 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Name: OEM04; Label: OEM04; Value: 19 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Name: OEM05; Label: OEM05; Value: 20 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Name: OEM06; Label: OEM06; Value: 21 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Name: OEM07; Label: OEM07; Value: 22 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Name: OEM08; Label: OEM08; Value: 23 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Name: OEM09; Label: OEM09; Value: 24 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Name: OEM10; Label: OEM10; Value: 25 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Name: OEM11; Label: OEM11; Value: 26 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Name: OEM12; Label: OEM12; Value: 27 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Name: OEM13; Label: OEM13; Value: 28 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Name: OEM14; Label: OEM14; Value: 29 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Name: OEM15; Label: OEM15; Value: 30 |  | Reserved for OEM use
bitfield32 | Evt |  |  | Label: OEM16; Value: 30 |  | Reserved for OEM use
enum16 | Alg |  |  | Name: NONE; Label: NONE; Value: 0 |  | No digital signature | For test purposes only
enum16 | Alg |  |  | Name: AES-GMAC-64; Label: AES-GMAC-64; Value: 1 |  | 64 bit AES signature algorithm is used
enum16 | Alg |  |  | Name: ECC-256; Label: ECC-256; Value: 2 |  | 256 bit ECC signature algorithm is used

## 302
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Irradiance Model | 302 | uint16 |  |  | R | M | Include to support various irradiance measurements
Header |  | 1 |  | 1 | L |  | 5 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | GHI | GHI |  | uint16 | W/m2 |  | R | O | Global Horizontal Irradiance
Fixed Block |  | 3 | 1 | 1 | POAI | POAI |  | uint16 | W/m2 |  | R | O | Plane-of-Array Irradiance
Fixed Block |  | 4 | 2 | 1 | DFI | DFI |  | uint16 | W/m2 |  | R | O | Diffuse Irradiance
Fixed Block |  | 5 | 3 | 1 | DNI | DNI |  | uint16 | W/m2 |  | R | O | Direct Normal Irradiance
Fixed Block |  | 6 | 4 | 1 | OTI | OTI |  | uint16 | W/m2 |  | R | O | Other Irradiance

## 303
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Back of Module Temperature Model | 303 | uint16 |  |  | R | M | Include to support variable number of back of module temperature measurements
Header |  | 1 |  | 1 | L |  | (RB Count * 1) | uint16 |  |  | R | M | Model Length
Repeating Block |  | 2 | 0 | 1 | TmpBOM | Temp |  | int16 | C | -1 | R | M | Back of module temperature measurement

## 304
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Inclinometer Model | 304 | uint16 |  |  | R | M | Include to support orienation measurements
Header |  | 1 |  | 1 | L |  | (RB Count * 6) | uint16 |  |  | R | M | Model Length
Repeating Block |  | 2 | 0 | 2 | Inclx | X |  | int32 | Degrees | -2 | R | M | X-Axis inclination
Repeating Block |  | 4 | 2 | 2 | Incly | Y |  | int32 | Degrees | -2 | R | O | Y-Axis inclination
Repeating Block |  | 6 | 4 | 2 | Inclz | Z |  | int32 | Degrees | -2 | R | O | Z-Axis inclination

## 305
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | GPS | 305 | uint16 |  |  | R | M | Include to support location measurements
Header |  | 1 |  | 1 | L |  | 36 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 6 | Tm | Tm |  | string | hhmmss.sssZ |  | R | O | UTC 24 hour time stamp to millisecond hhmmss.sssZ format
Fixed Block |  | 8 | 6 | 4 | Date | Date |  | string | YYYYMMDD |  | R | O | UTC Date string YYYYMMDD format
Fixed Block |  | 12 | 10 | 20 | Loc | Location |  | string | text |  | R | O | Location string (40 chars max)
Fixed Block |  | 32 | 30 | 2 | Lat | Lat |  | int32 | Degrees | -7 | R | O | Lattitude with seven degrees of precision
Fixed Block |  | 34 | 32 | 2 | Long | Long |  | int32 | Degrees | -7 | R | O | Longitude with seven degrees of precision
Fixed Block |  | 36 | 34 | 2 | Alt | Altitude |  | int32 | meters |  | R | O | Altitude measurement in meters

## 306
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Reference Point Model | 306 | uint16 |  |  | R | M | Include to support a standard reference point
Header |  | 1 |  | 1 | L |  | 4 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | GHI | GHI |  | uint16 | W/m2 |  | R | O | Global Horizontal Irrandiance
Fixed Block |  | 3 | 1 | 1 | A | Amps |  | uint16 | W/m2 |  | R | O | Current measurment at reference point
Fixed Block |  | 4 | 2 | 1 | V | Voltage |  | uint16 | W/m2 |  | R | O | Voltage measurment at reference point
Fixed Block |  | 5 | 3 | 1 | Tmp | Temperature |  | uint16 | W/m2 |  | R | O | Temperature measurment at reference point

## 307
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Base Met | 307 | uint16 |  |  | R | M | Base Meteorolgical Model | This model supersedes model 301
Header |  | 1 |  | 1 | L |  | 11 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | TmpAmb | Ambient Temperature |  | int16 | C | -1 | R | O
Fixed Block |  | 3 | 1 | 1 | RH | Relative Humidity |  | int16 | Pct |  | R | O
Fixed Block |  | 4 | 2 | 1 | Pres | Barometric Pressure |  | int16 | HPa |  | R | O
Fixed Block |  | 5 | 3 | 1 | WndSpd | Wind Speed |  | int16 | mps |  | R | O
Fixed Block |  | 6 | 4 | 1 | WndDir | Wind Direction |  | int16 | deg |  | R | O
Fixed Block |  | 7 | 5 | 1 | Rain | Rainfall |  | int16 | mm |  | R | O
Fixed Block |  | 8 | 6 | 1 | Snw | Snow Depth |  | int16 | mm |  | R | O
Fixed Block |  | 9 | 7 | 1 | PPT | Precipitation Type |  | int16 |  |  | R | O | Precipitation Type (WMO 4680 SYNOP code reference)
Fixed Block |  | 10 | 8 | 1 | ElecFld | Electric Field |  | int16 | Vm |  | R | O
Fixed Block |  | 11 | 9 | 1 | SurWet | Surface Wetness |  | int16 | kO |  | R | O
Fixed Block |  | 12 | 10 | 1 | SoilWet | Soil Wetness |  | int16 | Pct |  | R | O

## 308
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Mini Met Model | 308 | uint16 |  |  | R | M | Include to support a few basic measurements
Header |  | 1 |  | 1 | L |  | 4 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | GHI | GHI |  | uint16 | W/m2 |  | R | O | Global Horizontal Irradiance
Fixed Block |  | 3 | 1 | 1 | TmpBOM | Temp |  | int16 | C | -1 | R | O | Back of module temperature measurement
Fixed Block |  | 4 | 2 | 1 | TmpAmb | Ambient Temperature |  | int16 | C | -1 | R | O
Fixed Block |  | 5 | 3 | 1 | WndSpd | Wind Speed |  | uint16 | m/s |  | R | O

## 401
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | String Combiner (Current) | 401 | uint16 |  |  | R | M | A basic string combiner | This model is SUPERSEDED by model 403
Header |  | 1 |  | 1 | L |  | 14 + (RB Count * 8) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | Size: 1; Name: DCA_SF; Type: sunssf; R/W: R | M | Current scale factor
Fixed Block |  | 3 | 1 | Size: 1; Name: DCAhr_SF; Type: sunssf; R/W: R | O | Amp-hour scale factor
Fixed Block |  | 4 | 2 | Size: 1; Name: DCV_SF; Type: sunssf; R/W: R | O | Voltage scale factor
Fixed Block |  | 5 | 3 | 1 | DCAMax | Rating |  | uint16 | A | DCA_SF | R | M | Maximum DC Current Rating
Fixed Block |  | 6 | 4 | 1 | N | N |  | count |  |  | R | M | Number of Inputs
Fixed Block |  | 7 | 5 | 2 | Evt | Event |  | bitfield32 |  |  | R | M | Bitmask value. Events
Fixed Block |  | 9 | 7 | 2 | EvtVnd | Vendor Event |  | bitfield32 |  |  | R | O | Bitmask value. Vendor defnied events
Fixed Block |  | 11 | 9 | 1 | DCA | Amps |  | int16 | A | DCA_SF | R | M | Total measured current
Fixed Block |  | 12 | 10 | 2 | DCAhr | Amp-hours |  | uint32 | Ah | DCAhr_SF | R | O | Total metered Amp-hours
Fixed Block |  | 14 | 12 | 1 | DCV | Voltage |  | uint16 | V | DCV_SF | R | O | Output Voltage
Fixed Block |  | 15 | 13 | 1 | Tmp | Temp |  | int16 | C |  | R | O | Internal operating temperature
Repeating Block |  | 16 | 0 | 1 | InID | ID |  | uint16 |  |  | R | M | Uniquely identifies this input set
Repeating Block |  | 17 | 1 | 2 | InEvt | Event |  | bitfield32 |  |  | R | M | String Input Event Flags
Repeating Block |  | 19 | 3 | 2 | InEvtVnd | Vendor Event |  | bitfield32 |  |  | R | O | String Input Vendor Event Flags
Repeating Block |  | 21 | 5 | 1 | InDCA | Amps |  | int16 | A | DCA_SF | R | M | String Input Current
Repeating Block |  | 22 | 6 | 2 | InDCAhr | Amp-hours |  | uint32 | Ah | DCAhr_SF | R | O | String Input Amp-Hours
bitfield32 | Evt |  |  | Name: LOW_VOLTAGE; Value: 0
bitfield32 | Evt |  |  | Name: LOW_POWER; Value: 1
bitfield32 | Evt |  |  | Name: LOW_EFFICIENCY; Value: 2
bitfield32 | Evt |  |  | Name: CURRENT; Value: 3
bitfield32 | Evt |  |  | Name: VOLTAGE; Value: 4
bitfield32 | Evt |  |  | Name: POWER; Value: 5
bitfield32 | Evt |  |  | Name: PR; Value: 6
bitfield32 | Evt |  |  | Name: DISCONNECTED; Value: 7
bitfield32 | Evt |  |  | Name: FUSE_FAULT; Value: 8
bitfield32 | Evt |  |  | Name: COMBINER_FUSE_FAULT; Value: 9
bitfield32 | Evt |  |  | Name: COMBINER_CABINET_OPEN; Value: 10
bitfield32 | Evt |  |  | Name: TEMP; Value: 11
bitfield32 | Evt |  |  | Name: GROUNDFAULT; Value: 12
bitfield32 | Evt |  |  | Name: REVERSED_POLARITY; Value: 13
bitfield32 | Evt |  |  | Name: INCOMPATIBLE; Value: 14
bitfield32 | Evt |  |  | Name: COMM_ERROR; Value: 15
bitfield32 | Evt |  |  | Name: INTERNAL_ERROR; Value: 16
bitfield32 | Evt |  |  | Name: THEFT; Value: 17
bitfield32 | Evt |  |  | Name: ARC_DETECTED; Value: 18
bitfield32 | InEvt |  |  | Name: LOW_VOLTAGE; Value: 0
bitfield32 | InEvt |  |  | Name: LOW_POWER; Value: 1
bitfield32 | InEvt |  |  | Name: LOW_EFFICIENCY; Value: 2
bitfield32 | InEvt |  |  | Name: CURRENT; Value: 3
bitfield32 | InEvt |  |  | Name: VOLTAGE; Value: 4
bitfield32 | InEvt |  |  | Name: POWER; Value: 5
bitfield32 | InEvt |  |  | Name: PR; Value: 6
bitfield32 | InEvt |  |  | Name: DISCONNECTED; Value: 7
bitfield32 | InEvt |  |  | Name: FUSE_FAULT; Value: 8
bitfield32 | InEvt |  |  | Name: COMBINER_FUSE_FAULT; Value: 9
bitfield32 | InEvt |  |  | Name: COMBINER_CABINET_OPEN; Value: 10
bitfield32 | InEvt |  |  | Name: TEMP; Value: 11
bitfield32 | InEvt |  |  | Name: GROUNDFAULT; Value: 12
bitfield32 | InEvt |  |  | Name: REVERSED_POLARITY; Value: 13
bitfield32 | InEvt |  |  | Name: INCOMPATIBLE; Value: 14
bitfield32 | InEvt |  |  | Name: COMM_ERROR; Value: 15
bitfield32 | InEvt |  |  | Name: INTERNAL_ERROR; Value: 16
bitfield32 | InEvt |  |  | Name: THEFT; Value: 17
bitfield32 | InEvt |  |  | Name: ARC_DETECTED; Value: 18

## 402
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | String Combiner (Advanced) | 402 | uint16 |  |  | R | M | An advanced string combiner | This model is SUPERSEDED by model 404
Header |  | 1 |  | 1 | L |  | 20 + (RB Count * 14) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | Size: 1; Name: DCA_SF; Type: sunssf; R/W: R | M | Current scale factor
Fixed Block |  | 3 | 1 | Size: 1; Name: DCAhr_SF; Type: sunssf; R/W: R | O | Amp-hour scale factor
Fixed Block |  | 4 | 2 | Size: 1; Name: DCV_SF; Type: sunssf; R/W: R | O | Voltage scale factor
Fixed Block |  | 5 | 3 | Size: 1; Name: DCW_SF; Type: sunssf; R/W: R | O | Power scale factor
Fixed Block |  | 6 | 4 | Size: 1; Name: DCWh_SF; Type: sunssf; R/W: R | M | Energy scale factor
Fixed Block |  | 7 | 5 | 1 | DCAMax | Rating |  | uint16 | A |  | R | O | Maximum DC Current Rating
Fixed Block |  | 8 | 6 | 1 | N | N |  | count |  |  | R | O | Number of Inputs
Fixed Block |  | 9 | 7 | 2 | Evt | Event |  | bitfield32 |  |  | R | M | Bitmask value. Events
Fixed Block |  | 11 | 9 | 2 | EvtVnd | Vendor Event |  | bitfield32 |  |  | R | O | Bitmask value. Vendor defnied events
Fixed Block |  | 13 | 11 | 1 | DCA | Amps |  | int16 | A | DCA_SF | R | M | Total measured current
Fixed Block |  | 14 | 12 | 2 | DCAhr | Amp-hours |  | uint32 | Ah | DCAhr_SF | R | O | Total metered Amp-hours
Fixed Block |  | 16 | 14 | 1 | DCV | Voltage |  | uint16 | V | DCV_SF | R | O | Output Voltage
Fixed Block |  | 17 | 15 | 1 | Tmp | Temp |  | int16 | C |  | R | O | Internal operating temperature
Fixed Block |  | 18 | 16 | 1 | DCW | Watts |  | int16 | W | DCW_SF | R | O | Output power
Fixed Block |  | 19 | 17 | 1 | DCPR | PR |  | uint16 | Pct |  | R | O | DC Performance ratio value
Fixed Block |  | 20 | 18 | 2 | DCWh | Watt-hours |  | uint32 | Wh | DCWh_SF | R | M | Output energy
Repeating Block |  | 22 | 0 | 1 | InID | ID |  | uint16 |  |  | R | M | Uniquely identifies this input set
Repeating Block |  | 23 | 1 | 2 | InEvt | Event |  | bitfield32 |  |  | R | M | String Input Event Flags
Repeating Block |  | 25 | 3 | Size: 2; Name: EvtVnd; Type: bitfield32; R/W: R | O
Repeating Block |  | 27 | 5 | 1 | InDCA | Amps |  | int16 | A | DCA_SF | R | M | String Input Current
Repeating Block |  | 28 | 6 | 2 | InDCAhr | Amp-hours |  | uint32 | Ah | DCAhr_SF | R | O | String Input Amp-Hours
Repeating Block |  | 30 | 8 | 1 | InDCV | Voltage |  | uint16 | V | DCV_SF | R | O | String Input Voltage
Repeating Block |  | 31 | 9 | 1 | InDCW | Watts |  | int16 | W | DCWh_SF | R | O | String Input Power
Repeating Block |  | 32 | 10 | 2 | InDCWh | Watt-hours |  | uint32 | Wh |  | R | O | String Input Energy
Repeating Block |  | 34 | 12 | 1 | InDCPR | PR |  | uint16 | Pct |  | R | O | String Performance Ratio
Repeating Block |  | 35 | 13 | 1 | InN | N |  | uint16 |  |  | R | O | Number of modules in this input string | Configured value
bitfield32 | Evt |  |  | Name: LOW_VOLTAGE; Value: 0
bitfield32 | Evt |  |  | Name: LOW_POWER; Value: 1
bitfield32 | Evt |  |  | Name: LOW_EFFICIENCY; Value: 2
bitfield32 | Evt |  |  | Name: CURRENT; Value: 3
bitfield32 | Evt |  |  | Name: VOLTAGE; Value: 4
bitfield32 | Evt |  |  | Name: POWER; Value: 5
bitfield32 | Evt |  |  | Name: PR; Value: 6
bitfield32 | Evt |  |  | Name: DISCONNECTED; Value: 7
bitfield32 | Evt |  |  | Name: FUSE_FAULT; Value: 8
bitfield32 | Evt |  |  | Name: COMBINER_FUSE_FAULT; Value: 9
bitfield32 | Evt |  |  | Name: COMBINER_CABINET_OPEN; Value: 10
bitfield32 | Evt |  |  | Name: TEMP; Value: 11
bitfield32 | Evt |  |  | Name: GROUNDFAULT; Value: 12
bitfield32 | Evt |  |  | Name: REVERSED_POLARITY; Value: 13
bitfield32 | Evt |  |  | Name: INCOMPATIBLE; Value: 14
bitfield32 | Evt |  |  | Name: COMM_ERROR; Value: 15
bitfield32 | Evt |  |  | Name: INTERNAL_ERROR; Value: 16
bitfield32 | Evt |  |  | Name: THEFT; Value: 17
bitfield32 | Evt |  |  | Name: ARC_DETECTED; Value: 18
bitfield32 | InEvt |  |  | Name: LOW_VOLTAGE; Value: 0
bitfield32 | InEvt |  |  | Name: LOW_POWER; Value: 1
bitfield32 | InEvt |  |  | Name: LOW_EFFICIENCY; Value: 2
bitfield32 | InEvt |  |  | Name: CURRENT; Value: 3
bitfield32 | InEvt |  |  | Name: VOLTAGE; Value: 4
bitfield32 | InEvt |  |  | Name: POWER; Value: 5
bitfield32 | InEvt |  |  | Name: PR; Value: 6
bitfield32 | InEvt |  |  | Name: DISCONNECTED; Value: 7
bitfield32 | InEvt |  |  | Name: FUSE_FAULT; Value: 8
bitfield32 | InEvt |  |  | Name: COMBINER_FUSE_FAULT; Value: 9
bitfield32 | InEvt |  |  | Name: COMBINER_CABINET_OPEN; Value: 10
bitfield32 | InEvt |  |  | Name: TEMP; Value: 11
bitfield32 | InEvt |  |  | Name: GROUNDFAULT; Value: 12
bitfield32 | InEvt |  |  | Name: REVERSED_POLARITY; Value: 13
bitfield32 | InEvt |  |  | Name: INCOMPATIBLE; Value: 14
bitfield32 | InEvt |  |  | Name: COMM_ERROR; Value: 15
bitfield32 | InEvt |  |  | Name: INTERNAL_ERROR; Value: 16
bitfield32 | InEvt |  |  | Name: THEFT; Value: 17
bitfield32 | InEvt |  |  | Name: ARC_DETECTED; Value: 18

## 403
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | String Combiner (Current) | 403 | uint16 |  |  | R | M | A basic string combiner model | This model supersedes model 401
Header |  | 1 |  | 1 | L |  | 16 + (RB Count * 8) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | Size: 1; Name: DCA_SF; Type: sunssf; R/W: R | M | Current scale factor
Fixed Block |  | 3 | 1 | Size: 1; Name: DCAhr_SF; Type: sunssf; R/W: R | O | Amp-hour scale factor
Fixed Block |  | 4 | 2 | Size: 1; Name: DCV_SF; Type: sunssf; R/W: R | O | Voltage scale factor
Fixed Block |  | 5 | 3 | 1 | DCAMax | Rating |  | uint16 | A | DCA_SF | R | M | Maximum DC Current Rating
Fixed Block |  | 6 | 4 | 1 | N | N |  | count |  |  | R | M | Number of Inputs
Fixed Block |  | 7 | 5 | 2 | Evt | Event |  | bitfield32 |  |  | R | M | Bitmask value. Events
Fixed Block |  | 9 | 7 | 2 | EvtVnd | Vendor Event |  | bitfield32 |  |  | R | O | Bitmask value. Vendor defnied events
Fixed Block |  | 11 | 9 | 1 | DCA | Amps |  | int16 | A | DCA_SF | R | M | Total measured current
Fixed Block |  | 12 | 10 | 2 | DCAhr | Amp-hours |  | acc32 | Ah | DCAhr_SF | R | O | Total metered Amp-hours
Fixed Block |  | 14 | 12 | 1 | DCV | Voltage |  | int16 | V | DCV_SF | R | O | Output Voltage
Fixed Block |  | 15 | 13 | 1 | Tmp | Temp |  | int16 | C |  | R | O | Internal operating temperature
Fixed Block |  | 16 | 14 | Size: 1; Name: InDCA_SF; Type: sunssf; R/W: R | O | Current scale factor for inputs
Fixed Block |  | 17 | 15 | Size: 1; Name: InDCAhr_SF; Type: sunssf; R/W: R | O | Amp-hour scale factor for inputs
Repeating Block |  | 18 | 0 | 1 | InID | ID |  | uint16 |  |  | R | M | Uniquely identifies this input set
Repeating Block |  | 19 | 1 | 2 | InEvt | Event |  | bitfield32 |  |  | R | M | String Input Event Flags
Repeating Block |  | 21 | 3 | 2 | InEvtVnd | Vendor Event |  | bitfield32 |  |  | R | O | String Input Vendor Event Flags
Repeating Block |  | 23 | 5 | 1 | InDCA | Amps |  | int16 | A | InDCA_SF | R | M | String Input Current
Repeating Block |  | 24 | 6 | 2 | InDCAhr | Amp-hours |  | acc32 | Ah | InDCAhr_SF | R | O | String Input Amp-Hours
bitfield32 | Evt |  |  | Name: LOW_VOLTAGE; Value: 0
bitfield32 | Evt |  |  | Name: LOW_POWER; Value: 1
bitfield32 | Evt |  |  | Name: LOW_EFFICIENCY; Value: 2
bitfield32 | Evt |  |  | Name: CURRENT; Value: 3
bitfield32 | Evt |  |  | Name: VOLTAGE; Value: 4
bitfield32 | Evt |  |  | Name: POWER; Value: 5
bitfield32 | Evt |  |  | Name: PR; Value: 6
bitfield32 | Evt |  |  | Name: DISCONNECTED; Value: 7
bitfield32 | Evt |  |  | Name: FUSE_FAULT; Value: 8
bitfield32 | Evt |  |  | Name: COMBINER_FUSE_FAULT; Value: 9
bitfield32 | Evt |  |  | Name: COMBINER_CABINET_OPEN; Value: 10
bitfield32 | Evt |  |  | Name: TEMP; Value: 11
bitfield32 | Evt |  |  | Name: GROUNDFAULT; Value: 12
bitfield32 | Evt |  |  | Name: REVERSED_POLARITY; Value: 13
bitfield32 | Evt |  |  | Name: INCOMPATIBLE; Value: 14
bitfield32 | Evt |  |  | Name: COMM_ERROR; Value: 15
bitfield32 | Evt |  |  | Name: INTERNAL_ERROR; Value: 16
bitfield32 | Evt |  |  | Name: THEFT; Value: 17
bitfield32 | Evt |  |  | Name: ARC_DETECTED; Value: 18
bitfield32 | InEvt |  |  | Name: LOW_VOLTAGE; Value: 0
bitfield32 | InEvt |  |  | Name: LOW_POWER; Value: 1
bitfield32 | InEvt |  |  | Name: LOW_EFFICIENCY; Value: 2
bitfield32 | InEvt |  |  | Name: CURRENT; Value: 3
bitfield32 | InEvt |  |  | Name: VOLTAGE; Value: 4
bitfield32 | InEvt |  |  | Name: POWER; Value: 5
bitfield32 | InEvt |  |  | Name: PR; Value: 6
bitfield32 | InEvt |  |  | Name: DISCONNECTED; Value: 7
bitfield32 | InEvt |  |  | Name: FUSE_FAULT; Value: 8
bitfield32 | InEvt |  |  | Name: COMBINER_FUSE_FAULT; Value: 9
bitfield32 | InEvt |  |  | Name: COMBINER_CABINET_OPEN; Value: 10
bitfield32 | InEvt |  |  | Name: TEMP; Value: 11
bitfield32 | InEvt |  |  | Name: GROUNDFAULT; Value: 12
bitfield32 | InEvt |  |  | Name: REVERSED_POLARITY; Value: 13
bitfield32 | InEvt |  |  | Name: INCOMPATIBLE; Value: 14
bitfield32 | InEvt |  |  | Name: COMM_ERROR; Value: 15
bitfield32 | InEvt |  |  | Name: INTERNAL_ERROR; Value: 16
bitfield32 | InEvt |  |  | Name: THEFT; Value: 17
bitfield32 | InEvt |  |  | Name: ARC_DETECTED; Value: 18

## 404
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | String Combiner (Advanced) | 404 | uint16 |  |  | R | M | An advanced string combiner including voltage and energy measurements | This model supersedes model 402
Header |  | 1 |  | 1 | L |  | 25 + (RB Count * 14) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | Size: 1; Name: DCA_SF; Type: sunssf; R/W: R | M | Current scale factor
Fixed Block |  | 3 | 1 | Size: 1; Name: DCAhr_SF; Type: sunssf; R/W: R | O | Amp-hour scale factor
Fixed Block |  | 4 | 2 | Size: 1; Name: DCV_SF; Type: sunssf; R/W: R | O | Voltage scale factor
Fixed Block |  | 5 | 3 | Size: 1; Name: DCW_SF; Type: sunssf; R/W: R | O | Power scale factor
Fixed Block |  | 6 | 4 | Size: 1; Name: DCWh_SF; Type: sunssf; R/W: R | O | Energy scale factor
Fixed Block |  | 7 | 5 | 1 | DCAMax | Rating |  | uint16 | A | DCA_SF | R | M | Maximum DC Current Rating
Fixed Block |  | 8 | 6 | 1 | N | N |  | count |  |  | R | M | Number of Inputs
Fixed Block |  | 9 | 7 | 2 | Evt | Event |  | bitfield32 |  |  | R | M | Bitmask value. Events
Fixed Block |  | 11 | 9 | 2 | EvtVnd | Vendor Event |  | bitfield32 |  |  | R | O | Bitmask value. Vendor defnied events
Fixed Block |  | 13 | 11 | 1 | DCA | Amps |  | int16 | A | DCA_SF | R | M | Total measured current
Fixed Block |  | 14 | 12 | 2 | DCAhr | Amp-hours |  | acc32 | Ah | DCAhr_SF | R | O | Total metered Amp-hours
Fixed Block |  | 16 | 14 | 1 | DCV | Voltage |  | int16 | V | DCV_SF | R | O | Output Voltage
Fixed Block |  | 17 | 15 | 1 | Tmp | Temp |  | int16 | C |  | R | O | Internal operating temperature
Fixed Block |  | 18 | 16 | 1 | DCW | Watts |  | int16 | W | DCW_SF | R | O | Output power
Fixed Block |  | 19 | 17 | 1 | DCPR | PR |  | int16 | Pct |  | R | O | DC Performance ratio value
Fixed Block |  | 20 | 18 | 2 | DCWh | Watt-hours |  | acc32 | Wh | DCWh_SF | R | O | Output energy
Fixed Block |  | 22 | 20 | Size: 1; Name: InDCA_SF; Type: sunssf; R/W: R | O | Current scale factor for inputs
Fixed Block |  | 23 | 21 | Size: 1; Name: InDCAhr_SF; Type: sunssf; R/W: R | O | Amp-hour scale factor for inputs
Fixed Block |  | 24 | 22 | Size: 1; Name: InDCV_SF; Type: sunssf; R/W: R | O | Voltage scale factor for inputs
Fixed Block |  | 25 | 23 | Size: 1; Name: InDCW_SF; Type: sunssf; R/W: R | O | Power scale factor for inputs
Fixed Block |  | 26 | 24 | Size: 1; Name: InDCWh_SF; Type: sunssf; R/W: R | O | Energy scale factor for inputs
Repeating Block |  | 27 | 0 | 1 | InID | ID |  | uint16 |  |  | R | M | Uniquely identifies this input set
Repeating Block |  | 28 | 1 | 2 | InEvt | Event |  | bitfield32 |  |  | R | M | String Input Event Flags
Repeating Block |  | 30 | 3 | 2 | InEvtVnd | Vendor Event |  | bitfield32 |  |  | R | O | String Input Vendor Event Flags
Repeating Block |  | 32 | 5 | 1 | InDCA | Amps |  | int16 | A | InDCA_SF | R | M | String Input Current
Repeating Block |  | 33 | 6 | 2 | InDCAhr | Amp-hours |  | acc32 | Ah | InDCAhr_SF | R | O | String Input Amp-Hours
Repeating Block |  | 35 | 8 | 1 | InDCV | Voltage |  | int16 | V | InDCV_SF | R | O | String Input Voltage
Repeating Block |  | 36 | 9 | 1 | InDCW | Watts |  | int16 | W | InDCW_SF | R | O | String Input Power
Repeating Block |  | 37 | 10 | 2 | InDCWh | Watt-hours |  | acc32 | Wh | InDCWh_SF | R | O | String Input Energy
Repeating Block |  | 39 | 12 | 1 | InDCPR | PR |  | uint16 | Pct |  | R | O | String Performance Ratio
Repeating Block |  | 40 | 13 | 1 | InN | N |  | uint16 |  |  | R | O | Number of modules in this input string | Configured value
bitfield32 | Evt |  |  | Name: LOW_VOLTAGE; Value: 0
bitfield32 | Evt |  |  | Name: LOW_POWER; Value: 1
bitfield32 | Evt |  |  | Name: LOW_EFFICIENCY; Value: 2
bitfield32 | Evt |  |  | Name: CURRENT; Value: 3
bitfield32 | Evt |  |  | Name: VOLTAGE; Value: 4
bitfield32 | Evt |  |  | Name: POWER; Value: 5
bitfield32 | Evt |  |  | Name: PR; Value: 6
bitfield32 | Evt |  |  | Name: DISCONNECTED; Value: 7
bitfield32 | Evt |  |  | Name: FUSE_FAULT; Value: 8
bitfield32 | Evt |  |  | Name: COMBINER_FUSE_FAULT; Value: 9
bitfield32 | Evt |  |  | Name: COMBINER_CABINET_OPEN; Value: 10
bitfield32 | Evt |  |  | Name: TEMP; Value: 11
bitfield32 | Evt |  |  | Name: GROUNDFAULT; Value: 12
bitfield32 | Evt |  |  | Name: REVERSED_POLARITY; Value: 13
bitfield32 | Evt |  |  | Name: INCOMPATIBLE; Value: 14
bitfield32 | Evt |  |  | Name: COMM_ERROR; Value: 15
bitfield32 | Evt |  |  | Name: INTERNAL_ERROR; Value: 16
bitfield32 | Evt |  |  | Name: THEFT; Value: 17
bitfield32 | Evt |  |  | Name: ARC_DETECTED; Value: 18
bitfield32 | InEvt |  |  | Name: LOW_VOLTAGE; Value: 0
bitfield32 | InEvt |  |  | Name: LOW_POWER; Value: 1
bitfield32 | InEvt |  |  | Name: LOW_EFFICIENCY; Value: 2
bitfield32 | InEvt |  |  | Name: CURRENT; Value: 3
bitfield32 | InEvt |  |  | Name: VOLTAGE; Value: 4
bitfield32 | InEvt |  |  | Name: POWER; Value: 5
bitfield32 | InEvt |  |  | Name: PR; Value: 6
bitfield32 | InEvt |  |  | Name: DISCONNECTED; Value: 7
bitfield32 | InEvt |  |  | Name: FUSE_FAULT; Value: 8
bitfield32 | InEvt |  |  | Name: COMBINER_FUSE_FAULT; Value: 9
bitfield32 | InEvt |  |  | Name: COMBINER_CABINET_OPEN; Value: 10
bitfield32 | InEvt |  |  | Name: TEMP; Value: 11
bitfield32 | InEvt |  |  | Name: GROUNDFAULT; Value: 12
bitfield32 | InEvt |  |  | Name: REVERSED_POLARITY; Value: 13
bitfield32 | InEvt |  |  | Name: INCOMPATIBLE; Value: 14
bitfield32 | InEvt |  |  | Name: COMM_ERROR; Value: 15
bitfield32 | InEvt |  |  | Name: INTERNAL_ERROR; Value: 16
bitfield32 | InEvt |  |  | Name: THEFT; Value: 17
bitfield32 | InEvt |  |  | Name: ARC_DETECTED; Value: 18

## 501
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Solar Module | 501 | uint16 |  |  | R | M | A solar module model supporing DC-DC converter | Float
Header |  | 1 |  | 1 | L |  | 31 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | Stat | Status |  | enum16 |  |  | R | M | Enumerated value. Module Status Code
Fixed Block |  | 3 | 1 | 1 | StatVend | Vendor Status |  | enum16 |  |  | R | O | Module Vendor Status Code
Fixed Block |  | 4 | 2 | 2 | Evt | Events |  | bitfield32 |  |  | R | M | Bitmask value. Module Event Flags
Fixed Block |  | 6 | 4 | 2 | EvtVend | Vendor Module Event Flags |  | bitfield32 |  |  | R | O | Vendor specific flags
Fixed Block |  | 8 | 6 | 1 | Ctl | Control |  | enum16 |  |  | RW | O | Module Control
Fixed Block |  | 9 | 7 | 2 | CtlVend | Vendor Control |  | enum32 |  |  | RW | O | Vendor Module Control
Fixed Block |  | 11 | 9 | 2 | CtlVal | Control Value |  | int32 |  |  | RW | O | Module Control Value
Fixed Block |  | 13 | 11 | 2 | Tms | Timestamp |  | uint32 | Secs |  | R | O | Time in seconds since 2000 epoch
Fixed Block |  | 15 | 13 | 2 | OutA | Output Current |  | float32 | A |  | R | O | Output Current
Fixed Block |  | 17 | 15 | 2 | OutV | Output Voltage |  | float32 | V |  | R | O | Output Voltage
Fixed Block |  | 19 | 17 | 2 | OutWh | Output Energy |  | float32 | Wh |  | R | O | Output Energy
Fixed Block |  | 21 | 19 | 2 | OutW | Output Power |  | float32 | W |  | R | O | Output Power
Fixed Block |  | 23 | 21 | 2 | Tmp | Temp |  | float32 | C |  | R | O | Module Temperature
Fixed Block |  | 25 | 23 | 2 | InA | Input Current |  | float32 | A |  | R | O | Input Current
Fixed Block |  | 27 | 25 | 2 | InV | Input Voltage |  | float32 | V |  | R | O | Input Voltage
Fixed Block |  | 29 | 27 | 2 | InWh | Input Energy |  | float32 | Wh |  | R | O | Input Energy
Fixed Block |  | 31 | 29 | 2 | InW | Input Power |  | float32 | W |  | R | O | Input Power
enum16 | Stat |  |  | Name: OFF; Label: Off; Value: 1 |  | Module is in the OFF state
enum16 | Stat |  |  | Name: SLEEPING; Label: SLEEPING; Value: 2 |  | Sleeping (auto-shutdown) or panel is at low/safe output power/voltage
enum16 | Stat |  |  | Name: STARTING; Label: STARTING; Value: 3 |  | Starting up or ON but not producting power; panel might have high voltage but is not producing power
enum16 | Stat |  |  | Name: MPPT; Label: MPPT; Value: 4 |  | Tracking MPPT power point
enum16 | Stat |  |  | Name: THROTTLED; Label: THROTTLED; Value: 5 |  | Forced power reduction / power de-rating
enum16 | Stat |  |  | Name: SHUTTING_DOWN; Label: SHUTTING_DOWN; Value: 6 |  | Shutting down
enum16 | Stat |  |  | Name: FAULT; Label: FAULT; Value: 7 |  | One or more faults exist
enum16 | Stat |  |  | Name: STANDBY; Label: STANDBY; Value: 8 |  | Standby (service or unit) - unlike SLEEPING in this mode the module might be at a high (unsafe) output voltage or power
enum16 | Stat |  |  | Name: TEST; Label: TEST; Value: 9 |  | Test mode
enum16 | Stat |  |  | Name: OTHER; Label: OTHER; Value: 10 |  | As defined in vendor specific status
bitfield32 | Evt |  |  | Name: GROUND_FAULT; Label: Ground Fault; Value: 0 |  | Ground Fault
bitfield32 | Evt |  |  | Name: INPUT_OVER_VOLTAGE; Label: Over Voltage; Value: 1 |  | DC input over-voltage
bitfield32 | Evt |  |  | Name: RESERVED; Label: Reserved; Value: 11 |  | Reserved | Reserved for u-inverter compatibility
bitfield32 | Evt |  |  | Name: DC_DISCONNECT; Label: Disconnect; Value: 3 |  | DC disconnect open
bitfield32 | Evt |  |  | Name: MANUAL_SHUTDOWN; Label: Manual shutdown; Value: 6 |  | Manual shutdown
bitfield32 | Evt |  |  | Name: OVER_TEMPERATURE; Label: Over Temperature; Value: 7 |  | Over Temperature
bitfield32 | Evt |  |  | Name: BLOWN_FUSE; Label: Blown Fuse; Value: 12 |  | Input fuse is blown
bitfield32 | Evt |  |  | Name: UNDER_TEMPERATURE; Label: Under Temperature; Value: 13 |  | Under Temperature
bitfield32 | Evt |  |  | Name: MEMORY_LOSS; Label: Memory Loss; Value: 14 |  | Generic Memory or Communication Error
bitfield32 | Evt |  |  | Name: ARC_DETECTION; Label: Arc Detection; Value: 15 |  | Arc Detection
bitfield32 | Evt |  |  | Name: THEFT_DETECTION; Label: Theft Detection; Value: 16 |  | Theft Detection
bitfield32 | Evt |  |  | Name: OUTPUT_OVER_CURRENT; Label: Over Current; Value: 17 |  | Output Over Current
bitfield32 | Evt |  |  | Name: OUTPUT_OVER_VOLTAGE; Label: Output Over Voltage; Value: 18 |  | DC Output Over Voltage
bitfield32 | Evt |  |  | Name: OUTPUT_UNDER_VOLTAGE; Label: Output Under Voltage; Value: 19 |  | DC Output Under Voltage
bitfield32 | Evt |  |  | Name: TEST_FAILED; Label: Test Failed; Value: 20 |  | Last Self Test failed; see vendor event for details

## 502
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Solar Module | 502 | uint16 |  |  | R | M | A solar module model supporing DC-DC converter | Integer
Header |  | 1 |  | 1 | L |  | 28 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | Size: 1; Name: A_SF; Type: sunssf; R/W: R | O | Current scale factor
Fixed Block |  | 3 | 1 | Size: 1; Name: V_SF; Type: sunssf; R/W: R | O | Voltage scale factor
Fixed Block |  | 4 | 2 | Size: 1; Name: W_SF; Type: sunssf; R/W: R | O | Power scale factor
Fixed Block |  | 5 | 3 | Size: 1; Name: Wh_SF; Type: sunssf; R/W: R | O | Energy scale factor
Fixed Block |  | 6 | 4 | 1 | Stat | Status |  | enum16 |  |  | R | M | Enumerated value. Module Status Code
Fixed Block |  | 7 | 5 | 1 | StatVend | Vendor Status |  | enum16 |  |  | R | O | Module Vendor Status Code
Fixed Block |  | 8 | 6 | 2 | Evt | Events |  | bitfield32 |  |  | R | M | Bitmask value. Module Event Flags
Fixed Block |  | 10 | 8 | 2 | EvtVend | Vendor Module Event Flags |  | bitfield32 |  |  | R | O | Vendor specific flags
Fixed Block |  | 12 | 10 | 1 | Ctl | Control |  | enum16 |  |  | RW | O | Module Control
Fixed Block |  | 13 | 11 | 2 | CtlVend | Vendor Control |  | enum32 |  |  | RW | O | Vendor Module Control
Fixed Block |  | 15 | 13 | 2 | CtlVal | Control Value |  | int32 |  |  | RW | O | Module Control Value
Fixed Block |  | 17 | 15 | 2 | Tms | Timestamp |  | uint32 | Secs |  | R | O | Time in seconds since 2000 epoch
Fixed Block |  | 19 | 17 | 1 | OutA | Output Current |  | int16 | A | A_SF | R | O | Output Current
Fixed Block |  | 20 | 18 | 1 | OutV | Output Voltage |  | int16 | V | V_SF | R | O | Output Voltage
Fixed Block |  | 21 | 19 | 2 | OutWh | Output Energy |  | acc32 | Wh | Wh_SF | R | O | Output Energy
Fixed Block |  | 23 | 21 | 1 | OutPw |  |  | int16 | W | W_SF | R | O
Fixed Block |  | 24 | 22 | 1 | Tmp | Temp |  | int16 | C |  | R | O | Module Temperature
Fixed Block |  | 25 | 23 | 1 | InA | Input Current |  | int16 | A | A_SF | R | O | Input Current
Fixed Block |  | 26 | 24 | 1 | InV | Input Voltage |  | int16 | V | V_SF | R | O | Input Voltage
Fixed Block |  | 27 | 25 | 2 | InWh | Input Energy |  | acc32 | Wh | Wh_SF | R | O | Input Energy
Fixed Block |  | 29 | 27 | 1 | InW | Input Power |  | int16 | W | W_SF | R | O | Input Power
enum16 | Stat |  |  | Name: OFF; Label: Off; Value: 1 |  | Module is in the OFF state
enum16 | Stat |  |  | Name: SLEEPING; Label: SLEEPING; Value: 2 |  | Sleeping (auto-shutdown) or panel is at low/safe output power/voltage
enum16 | Stat |  |  | Name: STARTING; Label: STARTING; Value: 3 |  | Starting up or ON but not producting power; panel might have high voltage but is not producing power
enum16 | Stat |  |  | Name: MPPT; Label: MPPT; Value: 4 |  | Tracking MPPT power point
enum16 | Stat |  |  | Name: THROTTLED; Label: THROTTLED; Value: 5 |  | Forced power reduction / power de-rating
enum16 | Stat |  |  | Name: SHUTTING_DOWN; Label: SHUTTING_DOWN; Value: 6 |  | Shutting down
enum16 | Stat |  |  | Name: FAULT; Label: FAULT; Value: 7 |  | One or more faults exist
enum16 | Stat |  |  | Name: STANDBY; Label: STANDBY; Value: 8 |  | Standby (service or unit) - unlike SLEEPING in this mode the module might be at a high (unsafe) output voltage or power
enum16 | Stat |  |  | Name: TEST; Label: TEST; Value: 9 |  | Test mode
enum16 | Stat |  |  | Name: OTHER; Label: OTHER; Value: 10 |  | As defined in vendor specific status
bitfield32 | Evt |  |  | Name: GROUND_FAULT; Label: Ground Fault; Value: 0 |  | Ground Fault
bitfield32 | Evt |  |  | Name: INPUT_OVER_VOLTAGE; Label: Over Voltage; Value: 1 |  | DC input over-voltage
bitfield32 | Evt |  |  | Name: RESERVED; Label: Reserved; Value: 11 |  | Reserved | Reserved for u-inverter compatibility
bitfield32 | Evt |  |  | Name: DC_DISCONNECT; Label: Disconnect; Value: 3 |  | DC disconnect open
bitfield32 | Evt |  |  | Name: MANUAL_SHUTDOWN; Label: Manual shutdown; Value: 6 |  | Manual shutdown
bitfield32 | Evt |  |  | Name: OVER_TEMPERATURE; Label: Over Temperature; Value: 7 |  | Over Temperature
bitfield32 | Evt |  |  | Name: BLOWN_FUSE; Label: Blown Fuse; Value: 12 |  | Input fuse is blown
bitfield32 | Evt |  |  | Name: UNDER_TEMPERATURE; Label: Under Temperature; Value: 13 |  | Under Temperature
bitfield32 | Evt |  |  | Name: MEMORY_LOSS; Label: Memory Loss; Value: 14 |  | Generic Memory or Communication Error
bitfield32 | Evt |  |  | Name: ARC_DETECTION; Label: Arc Detection; Value: 15 |  | Arc Detection
bitfield32 | Evt |  |  | Name: THEFT_DETECTION; Label: Theft Detection; Value: 16 |  | Theft Detection
bitfield32 | Evt |  |  | Name: OUTPUT_OVER_CURRENT; Label: Over Current; Value: 17 |  | Output Over Current
bitfield32 | Evt |  |  | Name: OUTPUT_OVER_VOLTAGE; Label: Output Over Voltage; Value: 18 |  | DC Output Over Voltage
bitfield32 | Evt |  |  | Name: OUTPUT_UNDER_VOLTAGE; Label: Output Under Voltage; Value: 19 |  | DC Output Under Voltage
bitfield32 | Evt |  |  | Name: TEST_FAILED; Label: Test Failed; Value: 20 |  | Last Self Test failed; see vendor event for details

## 601
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Tracker Controller DRAFT 2 | 601 | uint16 |  |  | R | M | Monitors and controls multiple trackers | Trackers may include GPS model 305 for location information
Header |  | 1 |  | 1 | L |  | 26 + (RB Count * 22) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 8 | Nam | Controller |  | string |  |  | R | O | Descriptive name for this control unit
Fixed Block |  | 10 | 8 | 1 | Typ | Type |  | enum16 |  |  | R | M | Type of tracker
Fixed Block |  | 11 | 9 | 5 | DtLoc | Date |  | string | YYYYMMDD |  | R | O | Local date in YYYYMMDD format
Fixed Block |  | 16 | 14 | 3 | TmLoc | Time |  | string | hhmmss |  | R | O | 24 hour local time stamp to second
Fixed Block |  | 19 | 17 | 1 | Day | Day |  | uint16 |  |  | R | O | Number of the day in the year (1-366)
Fixed Block |  | 20 | 18 | 2 | GlblElCtl | Manual Elevation |  | int32 | Degrees | Dgr_SF | RW | O | Global manual override target position of elevation in degreees from horizontal. Unimplemented for single axis azimuth tracker type
Fixed Block |  | 22 | 20 | 2 | GlblAzCtl | Manual Azimuth |  | int32 | Degrees | Dgr_SF | RW | O | Global manual override target position of azimuth in degrees from true north towards east. Unimplemented for single axis azimuth tracker type
Fixed Block |  | 24 | 22 | 1 | GlblCtl | Mode |  | enum16 |  |  | RW | O | Global Control register operates on all trackers. Normal operation is automatic. Operator can override the position by setting the ElCtl, AzCtl and enabling Manual operation. Entering calibration mode will revert to automatic operation after calibration is complete.
Fixed Block |  | 25 | 23 | 1 | GlblAlm | Alarm |  | bitfield16 |  |  | R | O | Global tracker alarm conditions
Fixed Block |  | 26 | 24 | 1 | Dgr_SF | SF |  | sunssf |  |  | R | M | Scale Factor for targets and position measurements in degrees
Fixed Block |  | 27 | 25 | 1 | N | Trackers |  | uint16 |  |  | R | M | Number of trackers being controlled. Size of repeating block.
Repeating Block |  | 28 | 0 | 8 | Id | Tracker |  | string |  |  | R | O | Descriptive name for this tracker unit
Repeating Block |  | 36 | 8 | 2 | ElTrgt | Target Elevation |  | int32 | Degrees | Dgr_SF | R | O | Auto target elevation in degrees from horizontal. Unimplemented for single axis azimuth tracker type | Conformant implementations shall implement El or Az
Repeating Block |  | 38 | 10 | 2 | AzTrgt | Target Azimuth |  | int32 | Degrees | SF | R | O | Auto target azimuth in degrees from true north towards east. Unimplemented for single axis horizontal tracker type | Conformant implementations shall implement El or Az
Repeating Block |  | 40 | 12 | 2 | ElPos | Elevation |  | int32 | Degrees | Dgr_SF | R | O | Actual elevation position in degrees from horizontal. Unimplemented for single axis azimuth tracker type | Conformant implementations shall implement El or Az
Repeating Block |  | 42 | 14 | 2 | AzPos | Azimuth |  | int32 | Degrees | Dgr_SF | R | O | Actual azimuth position in degrees from true north towards east. Unimplemented for single axis horizontal tracker type | Conformant implementations shall implement El or Az
Repeating Block |  | 44 | 16 | 2 | ElCtl | Manual Elevation |  | int32 | Degrees | Dgr_SF | RW | O | Manual override target position of elevation in degreees from horizontal. Unimplemented for single axis azimuth tracker type
Repeating Block |  | 46 | 18 | 2 | AzCtl | Manual Azimuth |  | int32 | Degrees | Dgr_SF | RW | O | Manual override target position of azimuth in degrees from true north towards east. Unimplemented for single axis azimuth tracker type
Repeating Block |  | 48 | 20 | 1 | Ctl | Mode |  | enum16 |  |  | RW | O | Control register. Normal operation is automatic. Operator can override the position by setting the ElCtl, AzCtl and enabling Manual operation. Entering calibration mode will revert to automatic operation after calibration is complete.
Repeating Block |  | 49 | 21 | 1 | Alm | Alarm |  | bitfield16 |  |  | R | O | Tracker alarm conditions
enum16 | Typ |  |  | Name: Unknown; Label: Unknown; Value: 0 |  | Not Set
enum16 | Typ |  |  | Name: Fixed; Label: Fixed; Value: 1 |  | Documented orientation information
enum16 | Typ |  |  | Name: Horizontal; Label: Horizontal; Value: 2 |  | Single Axis Horizontal
enum16 | Typ |  |  | Name: Tilted; Label: Tilted; Value: 3 |  | Single Axis Tilted Horizontal
enum16 | Typ |  |  | Name: Azimuth; Label: Azimuth; Value: 4 |  | Single Axis Azimuth
enum16 | Typ |  |  | Name: Dual; Label: Dual; Value: 5 |  | Dual Axis
enum16 | Typ |  |  | Name: Other; Label: Other; Value: 99 |  | Other type
enum16 | GlblCtl |  |  | Name: Automatic; Label: Auto; Value: 0 |  | Follow programmed path
enum16 | GlblCtl |  |  | Name: Manual; Label: Manual; Value: 1 |  | Go to a fixed position
enum16 | GlblCtl |  |  | Name: Calibrate; Label: Calibrate; Value: 2 |  | Execute test mode
bitfield16 | GlblAlm |  |  | Name: SetPoint; Label: SetPoint; Value: 0 |  | One or more trackers are NOT at SetPoint
bitfield16 | GlblAlm |  |  | Name: ObsEl; Label: ObsEl; Value: 1 |  | One or more trackers ELEVATION motor is obstructed
bitfield16 | GlblAlm |  |  | Name: ObsAz; Label: ObsAz; Value: 2 |  | One or more trackers AZIMUTH motor is obstructed
enum16 | Ctl |  |  | Name: Automatic; Label: Auto; Value: 0 |  | Follow programmed path
enum16 | Ctl |  |  | Name: Manual; Label: Manual; Value: 1 |  | Go to a fixed position
enum16 | Ctl |  |  | Name: Calibrate; Label: Calibrate; Value: 2 |  | Execute test mode
bitfield16 | Alm |  |  | Name: SetPoint; Label: SetPoint; Value: 0 |  | One or more trackers are NOT at SetPoint
bitfield16 | Alm |  |  | Name: ObsEl; Label: ObsEl; Value: 1 |  | One or more trackers ELEVATION motor is obstructed
bitfield16 | Alm |  |  | Name: ObsAz; Label: ObsAz; Value: 2 |  | One or more trackers AZIMUTH motor is obstructed

## 801
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Energy Storage Base Model | 801 | uint16 |  |  | R | M
Header |  | 1 |  | 1 | L |  | 22 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | DERTyp | Distributed Energy Resource Type |  | enum16 |  |  | R | M | Type of distributed energy resource device.
Fixed Block |  | 3 | 1 | 1 | WHRtg | Nameplate Energy Capacity |  | uint16 | Wh | WHRtg_SF | R | M | Nameplate energy capacity in DC watt-hours.
Fixed Block |  | 4 | 2 | 1 | WMaxChaRte | Nameplate Max Charge Rate |  | uint16 | W | WMaxChaDisCha_SF | R | M | Maximum rate of energy transfer into the storage device.
Fixed Block |  | 5 | 3 | 1 | WMaxDisChaRte | Namplate Max Discharge Rate |  | uint16 | W | WMaxChaDisCha_SF | R | M | Maximum rate of energy transfer out of the storage device.
Fixed Block |  | 6 | 4 | 1 | DisChaRte | Self Discharge Rate |  | uint16 | %WHRtg | DisChaRte_SF | R | O | Self discharge rate. Percentage of capacity (WHRtg) discharged per day.
Fixed Block |  | 7 | 5 | 1 | SoCNpMaxPct | Nameplate Max SoC |  | uint16 | %WHRtg | SoC_SF | R | O | Manufacturer maximum state of charge, expressed as a percentage.
Fixed Block |  | 8 | 6 | 1 | SoCNpMinPct | Nameplate Min SoC |  | uint16 | %WHRtg | SoC_SF | R | O | Manufacturer minimum state of charge, expressed as a percentage.
Fixed Block |  | 9 | 7 | 1 | MaxRsvPct | Maximum Reserve Percent |  | uint16 | %WHRtg | SoC_SF | RW | O | Setpoint for maximum reserve for storage as a percentage of the nominal maximum storage.
Fixed Block |  | 10 | 8 | 1 | MinRsvPct | Minimum Reserve Percent |  | uint16 | %WHRtg | SoC_SF | RW | O | Setpoint for maximum reserve for storage as a percentage of the nominal maximum storage.
Fixed Block |  | 11 | 9 | 1 | SoC | State of Charge |  | uint16 | %WHRtg | SoC_SF | R | M | State of charge, expressed as a percentage. | Measurement
Fixed Block |  | 12 | 10 | 1 | ChaSt | ChaSt |  | enum16 |  |  | R | O | Charge status of storage device. Enumerated value.
Fixed Block |  | 13 | 11 | 1 | LocRemCtl | Control Mode |  | enum16 |  |  | R | M | DER control mode. Enumeration. | Maps to DRCC.LocRemCtl in 61850.
Fixed Block |  | 14 | 12 | 2 | Evt | Event Bitfield |  | bitfield32 |  |  | R | M | Bitmask value. Event fields.
Fixed Block |  | 16 | 14 | 1 | DERHb | Distributed Energy Resource Heartbeat |  | uint16 |  |  | RW | O | Value is incremented every second with periodic resets to zero.
Fixed Block |  | 17 | 15 | 1 | ControllerHb | Controller Heartbeat |  | uint16 |  |  | RW | O | Value is incremented every second with periodic resets to zero.
Fixed Block |  | 18 | 16 | 1 | DERAlarmReset | Alarm Reset |  | uint16 |  |  | R | O | Used to reset any latched alarms. 1 = Reset.
Fixed Block |  | 19 | 17 | Size: 1; Name: WHRtg_SF; Type: sunssf; R/W: R | M | Scale factor for energy capacity.
Fixed Block |  | 20 | 18 | Size: 1; Name: WMaxChaDisCha_SF; Type: sunssf; R/W: R | M | Scale factor for maximum charge and discharge rate.
Fixed Block |  | 21 | 19 | Size: 1; Name: DisChaRte_SF; Type: sunssf; R/W: R | O | Scale factor for self discharge rate.
Fixed Block |  | 22 | 20 | Size: 1; Name: SoC_SF; Type: sunssf; R/W: R | M | Scale factor for state of charge values.
Fixed Block |  | 23 | 21 | Size: 1; Name: Pad; Type: pad; R/W: R | M | Padding
enum16 | DERTyp |  |  | Name: STORAGE; Label: Storage Device; Value: 90 |  | A generic energy storage device. | Not yet a part of IEC 61850 DERTyp.
enum16 | DERTyp |  |  | Name: BATTERY; Label: Battery Device; Value: 91 |  | A generic battery. | Not yet a part of IEC 61850 DERTyp.
enum16 | DERTyp |  |  | Name: LITHIUM-ION BATTERY; Label: Lithium-ion Battery Device; Value: 92 |  | A lithium-ion battery. | Not yet a part of IEC 61850 DERTyp.
enum16 | DERTyp |  |  | Name: REDOX FLOW BATTERY; Label: Redox Flow Battery Device; Value: 93 |  | A redox flow battery. | Not yet a part of IEC 61850 DERTyp.
enum16 | ChaSt |  |  | Name: OFF; Value: 1
enum16 | ChaSt |  |  | Name: EMPTY; Value: 2
enum16 | ChaSt |  |  | Name: DISCHARGING; Value: 3
enum16 | ChaSt |  |  | Name: CHARGING; Value: 4
enum16 | ChaSt |  |  | Name: FULL; Value: 5
enum16 | ChaSt |  |  | Name: HOLDING; Value: 6
enum16 | ChaSt |  |  | Name: TESTING; Value: 7
enum16 | LocRemCtl |  |  | Name: REMOTE; Label: Remote Control; Value: 1 |  | Battery is controlled remotely (e.g. by the site controller). | Value of 0 matches LocRemCtl in 61850.
enum16 | LocRemCtl |  |  | Name: LOCAL; Label: Local Control; Value: 2 |  | Battery is controlled by a local operator (e.g. through battery HMI). | Value of 1 matches LocRemCtl in 61850.
bitfield32 | Evt |  |  | Name: UNDER_SOC_MIN_WARNING; Label: Under State of Charge Minimum Warning; Value: 0 |  | Battery state of charge is approaching SoCNpMinPct
bitfield32 | Evt |  |  | Name: UNDER_SOC_MIN_ALARM; Label: Under State of Charge Minimum Alarm; Value: 1 |  | Battery state of charge has reached or exceeded SoCNpMinPct
bitfield32 | Evt |  |  | Name: OVER_SOC_MAX_WARNING; Label: Over State of Charge Maximum Warning; Value: 2 |  | Battery state of charge is approaching SoCNpMaxPct
bitfield32 | Evt |  |  | Name: OVER_SOC_MAX_ALARM; Label: Over State of Charge Maximum Warning; Value: 3 |  | Battery state of charge has reached or exceeded SocNpMaxPct

## 802
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Battery Base Model | 802 | uint16 |  |  | R | M
Header |  | 1 |  | 1 | L |  | 20 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | BatTyp | Battery Type |  | enum16 |  |  | R | M | Type of battery. Enumeration. | Maps to DBAT in 61850.
Fixed Block |  | 3 | 1 | 1 | BatSt | State of the Battery Bank |  | enum16 |  |  | R | M | State of the battery bank. Enumeration. | Must be reconciled with BatSt in IEC 61850.
Fixed Block |  | 4 | 2 | 2 | CycleCt | Cycle Count |  | uint32 |  |  | R | O | Number of cycles executed in the battery.
Fixed Block |  | 6 | 4 | 1 | SoH | State of Health |  | uint16 | % | SoH_SF | R | O | Percentage of battery life remaining.
Fixed Block |  | 7 | 5 | 2 | Evt1 | Battery Event 1 Bitfield |  | bitfield32 |  |  | R | M | Alarms and warnings. Bit flags.
Fixed Block |  | 9 | 7 | 2 | Evt2 | Battery Event 2 Bitfield |  | bitfield32 |  |  | R | M | Alarms and warnings. Bit flags. | Reserved for future use.
Fixed Block |  | 11 | 9 | 1 | Vol | External Battery Voltage |  | uint16 | V | Vol_SF | R | M | DC Bus Voltage | Measurement. Maps to ZBAT.Vol.
Fixed Block |  | 12 | 10 | 1 | MaxBatACha | Max Charge Current |  | uint16 | A | MaxBatA_SF | R | M | Instantaneous maximum DC charge current. | Calculation. Nearly maps to ZBAT.MaxBatA.
Fixed Block |  | 13 | 11 | 1 | MaxBatADischa | Max Discharge Current |  | uint16 | A | MaxBatA_SF | R | M | Instantaneous maximum DC discharge current. | Calculation. Nearly maps to ZBAT.MaxBatA.
Fixed Block |  | 14 | 12 | 1 | BatReqPCSSt | PCS State Request |  | enum16 |  |  | R | O | Request from battery to start or stop the PCS. Enumeration. | Used in special states such as manual battery charging.
Fixed Block |  | 15 | 13 | 1 | BatReqW | Battery Power Request |  | int16 | W | BatReqW_SF | R | O | AC Power requested by battery. | Used in special states such as string balancing.
Fixed Block |  | 16 | 14 | 1 | BSetOperation | Set Operation |  | enum16 |  |  | RW | M | Instruct the battery bank to perform an operation such as connecting. Enumeration.
Fixed Block |  | 17 | 15 | 1 | BSetPCSState | PCS State |  | enum16 |  |  | RW | M | PCS State | Information needed by battery for some operations.
Fixed Block |  | 18 | 16 | Size: 1; Name: SoH_SF; Type: sunssf; R/W: R | O | Scale factor for State of Health.
Fixed Block |  | 19 | 17 | Size: 1; Name: Vol_SF; Type: sunssf; R/W: R | M | Scale factor for DC Bus Voltage.
Fixed Block |  | 20 | 18 | Size: 1; Name: MaxBatA_SF; Type: sunssf; R/W: R | M | Scale factor for instantationous DC charge/discharge current.
Fixed Block |  | 21 | 19 | Size: 1; Name: BatReqW_SF; Type: sunssf; R/W: R | O | Scale factor for AC power request.
enum16 | BatTyp |  |  | Name: NOT APPLICABLE_UNKNOWN; Label: Not Applicable or Unknown; Value: 0 |  | Battery type is not applicable or unknown.
enum16 | BatTyp |  |  | Name: LEAD_ACID; Label: Lead-Acid; Value: 1 |  | Lead-acid battery type.
enum16 | BatTyp |  |  | Name: NICKEL_METAL_HYDRATE; Label: Nickel-Metal Hydrate; Value: 2 |  | Nickel-metal hydrate battery type.
enum16 | BatTyp |  |  | Name: NICKEL_CADMIUM; Label: Nickel-Cadmium; Value: 3 |  | Nickel-cadmium battery type.
enum16 | BatTyp |  |  | Name: LITHIUM_ION; Label: Lithium-Ion; Value: 4 |  | Lithium-ion battery type.
enum16 | BatTyp |  |  | Name: CARBON_ZINC; Label: Carbon-Zinc; Value: 5 |  | Carbon-zinc battery type.
enum16 | BatTyp |  |  | Name: ZINC_CHLORIDE; Label: Zinc Chloride; Value: 6 |  | Zinc chloride battery type.
enum16 | BatTyp |  |  | Name: ALKALINE; Label: Alkaline; Value: 7 |  | Alkaline battery type.
enum16 | BatTyp |  |  | Name: RECHARGEABLE_ALKALINE; Label: Rechargeable Alkaline; Value: 8 |  | Rechargeable alkaline battery type.
enum16 | BatTyp |  |  | Name: SODIUM_SULFUR; Label: Sodium-Sulfur; Value: 9 |  | Sodium-sulfur battery type.
enum16 | BatTyp |  |  | Name: FLOW; Label: Flow; Value: 10 |  | Flow battery type.
enum16 | BatTyp |  |  | Name: OTHER; Label: Other; Value: 99 |  | Other battery type.
enum16 | BatSt |  |  | Name: DISCONNECTED; Label: Disconnected; Value: 1 |  | Battery bank is disconnected. All contactors are open.
enum16 | BatSt |  |  | Name: INITIALIZING; Label: Initializing; Value: 2 |  | Battery bank is initializing but not ready for operating. String balancing may occur.
enum16 | BatSt |  |  | Name: CONNECTED; Label: Connected; Value: 3 |  | Battery bank is ready for operation. All enabled contactors are closed.
enum16 | BatSt |  |  | Name: STANDBY; Label: Standby; Value: 4 |  | Battery bank is connected and in standby/power saving mode.
enum16 | BatSt |  |  | Name: SOC PROTECTION; Label: SOC Protection; Value: 5 |  | Battery bank is connected but SOC is too low. Battery should be considered "offline".
bitfield32 | Evt1 |  |  | Name: COMMUNICATION_ERROR; Label: Communication Error; Value: 0 |  | Unable to communcate with BMS or BMS is unable to communicate with battery strings.
bitfield32 | Evt1 |  |  | Name: OVER_TEMP_ALARM; Label: Over Temperature Alarm; Value: 1 |  | Battery has exceeded maximum operating temperature
bitfield32 | Evt1 |  |  | Name: UNDER_TEMP_ALARM; Label: Under Temperature Alarm; Value: 2 |  | Battery has exceeded minimum operating temperature
bitfield32 | Evt1 |  |  | Name: OVER_TEMP_WARNING; Label: Over Temperature Warning; Value: 3 |  | Battery is approaching maximum operating temperature.
bitfield32 | Evt1 |  |  | Name: UNDER_TEMP_WARNING; Label: Under Temperature Warning; Value: 4 |  | Battery is approaching minimum operating temperature.
bitfield32 | Evt1 |  |  | Name: OVER_CHARGE_CURRENT_ALARM; Label: Over Charge Current Alarm; Value: 5 |  | Battery maximum charge current has been exceeded. | See AMaxCha
bitfield32 | Evt1 |  |  | Name: OVER_DISCHARGE_CURRENT_ALARM; Label: Over Discharge Current Alarm; Value: 6 |  | Battery maximum discharge current has been exceeded. | See AMaxDischa
bitfield32 | Evt1 |  |  | Name: OVER_CHARGE_CURRENT_WARNING; Label: Over Charge Current Warning; Value: 7 |  | Approaching battery maximum charge current. | See AMaxCha
bitfield32 | Evt1 |  |  | Name: OVER_DISCHARGE_CURRENT_WARNING; Label: Over Discharge Current Warning; Value: 8 |  | Approaching battery maximum discharge current. | See AMaxDischa
bitfield32 | Evt1 |  |  | Name: VOLTAGE_IMBALANCE_WARNING; Label: Voltage Imbalance Warning; Value: 9 |  | A voltage imbalance exists between the strings in the battery bank.
bitfield32 | Evt1 |  |  | Name: CURRENT_IMBALANCE_WARNING; Label: Current Imbalance Warning; Value: 10 |  | A current imbalance exists between the strings in the battery bank.
bitfield32 | Evt1 |  |  | Name: OVER_VOLT_ALARM; Label: Over Voltage Alarm; Value: 11 |  | Battery voltage has exceeded maximum limit.
bitfield32 | Evt1 |  |  | Name: UNDER_VOLT_ALARM; Label: Under Voltage Alarm; Value: 12 |  | Battery voltage has exceeded minimum limit.
bitfield32 | Evt1 |  |  | Name: OVER_VOLT_WARNING; Label: Over Voltage Warning; Value: 13 |  | Battery voltage is approaching maximum limit.
bitfield32 | Evt1 |  |  | Name: UNDER_VOLT_WARNING; Label: Under Voltage Warning; Value: 14 |  | Battery voltage is approaching minimum limit.
bitfield32 | Evt1 |  |  | Name: CONTACTOR_ERROR; Label: Contactor Error; Value: 15 |  | A contactor failed to open or close as requested.
bitfield32 | Evt1 |  |  | Name: FAN_ERROR; Label: Fan Error; Value: 16 |  | One or more battery fans has failed.
bitfield32 | Evt1 |  |  | Name: CONTACTOR_STATUS; Label: Contactor Status; Value: 17 |  | String contactor is closed.
bitfield32 | Evt1 |  |  | Name: GROUND_FAULT; Label: Ground Fault Error; Value: 18 |  | Ground fault detected.
bitfield32 | Evt1 |  |  | Name: OPEN_DOOR_ERROR; Label: Open Door Error; Value: 19 |  | One or more door are open.
bitfield32 | Evt1 |  |  | Name: OTHER_ALARM; Label: Other Battery Alarm; Value: 20 |  | For manufacturer-specific alarms.
bitfield32 | Evt1 |  |  | Name: OTHER_WARNING; Label: Other Battery Warning; Value: 21 |  | For manufacturer-specific warnings.
enum16 | BatReqPCSSt |  |  | Name: NO REQUEST; Label: No Request; Value: 0 |  | Battery has no requests of the PCS.
enum16 | BatReqPCSSt |  |  | Name: START; Label: Start PCS; Value: 1 |  | Battery requests that the PCS be started. | Battery is notified of PCS state change through BSetPcsState.
enum16 | BatReqPCSSt |  |  | Name: STOP; Label: Stop PCS; Value: 2 |  | Battery requests that the PCS be stopped. | Battery is notified of PCS state change through BSetPcsState.
enum16 | BSetOperation |  |  | Name: CONNECT; Label: Connect the Battery Bank; Value: 1 |  | Initialize the battery bank and close contactors for all enabled strings.
enum16 | BSetOperation |  |  | Name: DISCONNECT; Label: Disconnect the Battery Bank; Value: 2 |  | Open contactors for all strings.
enum16 | BSetPCSState |  |  | Name: PCS_STOPPED; Label: PCS is Stopped; Value: 1
enum16 | BSetPCSState |  |  | Name: PCS_STANDBY; Label: PCS is in Standby; Value: 2
enum16 | BSetPCSState |  |  | Name: PCS_STARTED; Label: PCS is Started; Value: 3

## 803
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Lithium-Ion Battery Model | 803 | uint16 |  |  | R | M
Header |  | 1 |  | 1 | L |  | 16 + (RB Count * 16) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | BConStrCt | Connected String Count |  | uint16 |  |  | R | M | Number of strings with contactor closed.
Fixed Block |  | 3 | 1 | 1 | BMaxCellVol | Max Cell Voltage |  | uint16 | V | BCellVol_SF | R | M | Maximum voltage for all cells in the bank. | Measurement
Fixed Block |  | 4 | 2 | 1 | BMaxCellVolLoc | Max Cell Voltage Location |  | uint16 |  |  | R | O | Location of the cell with maximum voltage | Bit0:Bit7 = String Number Bit8:Bit15 = Module Number
Fixed Block |  | 5 | 3 | 1 | BMinCellVol | Min Cell Voltage |  | uint16 | V | BCellVol_SF | R | M | Minimum voltage for all cells in the bank. | Measurement
Fixed Block |  | 6 | 4 | 1 | BMinCellVolLoc | Min Cell Voltage Location |  | uint16 |  |  | R | O | Location of the cell with minimum voltage | Bit0:Bit7 = String Number Bit8:Bit15 = Module Number
Fixed Block |  | 7 | 5 | 1 | BMaxModTmp | Max Module Temp |  | int16 |  | BModTmp_SF | R | M | Maximum temperature for all modules in the bank. | Measurement
Fixed Block |  | 8 | 6 | 1 | BMaxModTmpLoc | Max Module Temp Location |  | uint16 |  |  | R | O | Location of the module with max temperature. | Bit0:Bit7 = String Number Bit8:Bit15 = Module Number
Fixed Block |  | 9 | 7 | 1 | BMinModTmp | Min Module Temp |  | int16 | C | BModTmp_SF | R | M | Minimum temperature for all modules in the bank. | Measurement
Fixed Block |  | 10 | 8 | 1 | BMinModTmpLoc | Min Module Temp Location |  | uint16 |  |  | R | O | Location of the module with min temperature. | Bit0:Bit7 = String Number Bit8:Bit15 = Module Number
Fixed Block |  | 11 | 9 | 1 | BTotDCCur | Total DC Current |  | int16 | A | BCurrent_SF | R | M | Total DC current flowing to/from the battery bank. | Measurement
Fixed Block |  | 12 | 10 | 1 | BMaxStrCur | Max String Current |  | int16 | A | BCurrent_SF | R | O | Maximum current of any string in the bank. | Measurement
Fixed Block |  | 13 | 11 | 1 | BMinStrCur | Min String Current |  | int16 | A | BCurrent_SF | R | O | Minimm current of any string in the bank. | Measurement
Fixed Block |  | 14 | 12 | Size: 1; Name: BCellVol_SF; Type: sunssf; R/W: R | M | Scale factor for cell voltage.
Fixed Block |  | 15 | 13 | Size: 1; Name: BModTmp_SF; Type: sunssf; R/W: R | M | Scale factor for module temperatures.
Fixed Block |  | 16 | 14 | Size: 1; Name: BCurrent_SF; Type: sunssf; R/W: R | M | Scale factor for Total DC Current, Max String Current and Min String Current.
Fixed Block |  | 17 | 15 | Size: 1; Name: StrSoH_SF; Type: sunssf; R/W: R | O | Scale factor for String State of Health.
Repeating Block |  | 18 | 0 | 1 | StrModCt | Module Count |  | uint16 |  |  | R | M | Count of modules in the string.
Repeating Block |  | 19 | 1 | 1 | StrSoC | String SoC |  | uint16 | % |  | R | M | Battery string state of charge, expressed as a percentage. | Measurement
Repeating Block |  | 20 | 2 | 1 | StrSoH | String SoH |  | uint16 | % | StrSoH_SF | R | O | Battery string state of health, expressed as a percentage. | Measurement
Repeating Block |  | 21 | 3 | 1 | StrCur | String Current |  | int16 | A | BCurrent_SF | R | M | String current measurement. | Measurement
Repeating Block |  | 22 | 4 | 1 | StrMaxCellVol | Max Cell Voltage |  | uint16 | V | BCellVol_SF | R | M | Maximum voltage for all cells in the string. | Measurement
Repeating Block |  | 23 | 5 | 1 | StrMinCellVol | Min Cell Voltage |  | uint16 | V | BCellVol_SF | R | M | Minimum voltage for all cells in the string. | Measurement
Repeating Block |  | 24 | 6 | 1 | StrCellVolLoc | Max/Min Cell Voltage Loc |  | uint16 |  |  | R | O | Location of maximum and minimum cell voltages. | Bit0:Bit7 = Max Module Num Bit8:Bit15 = Min Module Num
Repeating Block |  | 25 | 7 | 1 | StrMaxModTmp | Max Module Temp |  | int16 | C | BModTmp_SF | R | M | Maximum temperature for all modules in the bank. | Measurement
Repeating Block |  | 26 | 8 | 1 | StrMinModTmp | Min Module Temp |  | int16 | C | BModTmp_SF | R | M | Minimum temperature for all modules in the bank. | Measurement
Repeating Block |  | 27 | 9 | 1 | StrModTmpLoc | Max/Min Mod Temp Loc |  | uint16 |  |  | R | O | Location of maximum and minimum module temperatures. | Bit0:Bit7 = Max Module Num Bit8:Bit15 = Min Module Num
Repeating Block |  | 28 | 10 | 2 | StrEvt1 | String Event 1 |  | bitfield32 |  |  | R | M | Alarms, warnings and status values. Bit flags.
Repeating Block |  | 30 | 12 | 2 | StrEvt2 | String Event 2 |  | bitfield32 |  |  | R | O | Alarms, warnings and status values. Bit flags. | Reserved for future use.
Repeating Block |  | 32 | 14 | 1 | StrConFail | Connection Failure Reason |  | enum16 |  |  | R | O
Repeating Block |  | 33 | 15 | 1 | StrSetEna | Enable/Disable String |  | enum16 |  |  | RW | O | Enables and disables the string. Should reset to 0 upon completion.
bitfield32 | StrEvt1 |  |  | Name: COMMUNICATION_ERROR; Label: Communication Error; Value: 0 |  | Unable to communcate with BMS.
bitfield32 | StrEvt1 |  |  | Name: OVER_TEMP_ALARM; Label: Over Temperature Alarm; Value: 1 |  | Battery string has exceeded maximum operating temperature.
bitfield32 | StrEvt1 |  |  | Name: UNDER_TEMP_ALARM; Label: Under Temperature Alarm; Value: 2 |  | Battery string has exceeded minimum operating temperature.
bitfield32 | StrEvt1 |  |  | Name: OVER_TEMP_WARNING; Label: Over Temperature Warning; Value: 3 |  | Battery string is approaching maximum operating temperature.
bitfield32 | StrEvt1 |  |  | Name: UNDER_TEMP_WARNING; Label: Under Temperature Warning; Value: 4 |  | Battery string is approaching minimum operating temperature.
bitfield32 | StrEvt1 |  |  | Name: OVER_CHARGE_CURRENT_ALARM; Label: Over Charge Current Alarm; Value: 5 |  | Battery string maximum charge current has been exceeded. | See AMaxCha
bitfield32 | StrEvt1 |  |  | Name: OVER_DISCHARGE_CURRENT_ALARM; Label: Over Discharge Current Alarm; Value: 6 |  | Battery string maximum discharge current has been exceeded. | See AMaxDischa
bitfield32 | StrEvt1 |  |  | Name: OVER_CHARGE_CURRENT_WARNING; Label: Over Charge Current Warning; Value: 7 |  | Approaching battery string maximum charge current. | See AMaxCha
bitfield32 | StrEvt1 |  |  | Name: OVER_DISCHARGE_CURRENT_WARNING; Label: Over Discharge Current Warning; Value: 8 |  | Approaching battery string maximum discharge current. | See AMaxDischa
bitfield32 | StrEvt1 |  |  | Name: OVER_VOLT_ALARM; Label: Over Voltage Alarm; Value: 9 |  | Battery string voltage has exceeded maximum limit.
bitfield32 | StrEvt1 |  |  | Name: UNDER_VOLT_ALARM; Label: Under Voltage Alarm; Value: 10 |  | Battery string voltage has exceeded minimum limit.
bitfield32 | StrEvt1 |  |  | Name: OVER_VOLT_WARNING; Label: Over Voltage Warning; Value: 11 |  | Battery string voltage is approaching maximum limit.
bitfield32 | StrEvt1 |  |  | Name: UNDER_VOLT_WARNING; Label: Under Voltage Warning; Value: 12 |  | Battery string voltage is approaching minimum limit.
bitfield32 | StrEvt1 |  |  | Name: CONTACTOR_ERROR; Label: Contactor Error; Value: 13 |  | String contactor failed to open or close as requested.
bitfield32 | StrEvt1 |  |  | Name: FAN_ERROR; Label: Fan Error; Value: 14 |  | Battery string fan has failed.
bitfield32 | StrEvt1 |  |  | Name: CONTACTOR_STATUS; Label: Contactor Status; Value: 15 |  | String contactor is closed.
bitfield32 | StrEvt1 |  |  | Name: GROUND_FAULT; Label: Ground Fault Error; Value: 16 |  | Ground fault detected.
bitfield32 | StrEvt1 |  |  | Name: OPEN_DOOR_ERROR; Label: Open Door Error; Value: 17 |  | One or more door are open.
bitfield32 | StrEvt1 |  |  | Name: OTHER_ALARM; Label: Other Alarm; Value: 18 |  | An alarm has been triggered which does not map to one of the alarms above. | Operator should view battery HMI and/or logs for more information.
bitfield32 | StrEvt1 |  |  | Name: OTHER_WARNING; Label: Other Warning; Value: 19 |  | A warning has been triggered which does not map to one of the alarms above. | Operator should view battery HMI and/or logs for more information.
bitfield32 | StrEvt1 |  |  | Name: STRING_ENABLED; Label: String Enabled; Value: 20 |  | The string is currently enabled.
enum16 | StrConFail |  |  | Name: NO FAILURE; Value: 0 |  | Connect did not fail.
enum16 | StrConFail |  |  | Name: BUTTON_PUSHED; Value: 1 |  | A button was pushed which prevented connection.
enum16 | StrConFail |  |  | Name: STR_GROUND_FAULT; Value: 2 |  | Ground fault during auto-connect.
enum16 | StrConFail |  |  | Name: OUTSIDE_VOLTAGE_RANGE; Value: 3 |  | Outside voltage target window during auto-connect.
enum16 | StrSetEna |  |  | Name: ENABLE; Value: 1 |  | Enable the string.
enum16 | StrSetEna |  |  | Name: DISABLE; Value: 2 |  | Disable the string.

## 63001
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | SunSpec Test Model 1 | 63001 | uint16 |  |  | R | M
Header |  | 1 |  | 1 | L |  | 134 + (RB Count * 18) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | Size: 1; Name: sunssf_1; Type: sunssf; R/W: R | O
Fixed Block |  | 3 | 1 | Size: 1; Name: sunssf_2; Type: sunssf; R/W: R | O
Fixed Block |  | 4 | 2 | Size: 1; Name: sunssf_3; Type: sunssf; R/W: R | O
Fixed Block |  | 5 | 3 | Size: 1; Name: sunssf_4; Type: sunssf; R/W: R | O
Fixed Block |  | 6 | 4 | 1 | int16_1 |  |  | int16 |  | sunssf_1 | R | O
Fixed Block |  | 7 | 5 | 1 | int16_2 |  |  | int16 |  | sunssf_2 | R | O
Fixed Block |  | 8 | 6 | 1 | int16_3 |  |  | int16 |  | sunssf_3 | R | O
Fixed Block |  | 9 | 7 | 1 | int16_4 |  |  | int16 |  | sunssf_4 | RW | O
Fixed Block |  | 10 | 8 | Size: 1; Name: int16_5; Type: int16; R/W: R | O
Fixed Block |  | 11 | 9 | Size: 1; Name: int16_u; Type: int16; R/W: R | O
Fixed Block |  | 12 | 10 | 1 | uint16_1 |  |  | uint16 |  | sunssf_1 | R | O
Fixed Block |  | 13 | 11 | 1 | uint16_2 |  |  | uint16 |  | sunssf_2 | R | O
Fixed Block |  | 14 | 12 | 1 | uint16_3 |  |  | uint16 |  | sunssf_3 | R | O
Fixed Block |  | 15 | 13 | 1 | uint16_4 |  |  | uint16 |  | sunssf_4 | RW | O
Fixed Block |  | 16 | 14 | Size: 1; Name: uint16_5; Type: uint16; R/W: R | O
Fixed Block |  | 17 | 15 | Size: 1; Name: uint16_u; Type: uint16; R/W: R | O
Fixed Block |  | 18 | 16 | Size: 1; Name: acc16; Type: acc16; R/W: R | O
Fixed Block |  | 19 | 17 | Size: 1; Name: acc16_u; Type: acc16; R/W: R | O
Fixed Block |  | 20 | 18 | Size: 1; Name: enum16; Type: enum16; R/W: R | O
Fixed Block |  | 21 | 19 | Size: 1; Name: enum16_u; Type: enum16; R/W: R | O
Fixed Block |  | 22 | 20 | Size: 1; Name: bitfield16; Type: bitfield16; R/W: R | O
Fixed Block |  | 23 | 21 | Size: 1; Name: bitfield16_u; Type: bitfield16; R/W: R | O
Fixed Block |  | 24 | 22 | 2 | int32_1 |  |  | int32 |  | sunssf_5 | R | O
Fixed Block |  | 26 | 24 | 2 | int32_2 |  |  | int32 |  | sunssf_6 | R | O
Fixed Block |  | 28 | 26 | 2 | int32_3 |  |  | int32 |  | sunssf_7 | RW | O
Fixed Block |  | 30 | 28 | Size: 2; Name: int32_4; Type: int32; R/W: R | O
Fixed Block |  | 32 | 30 | Size: 2; Name: int32_5; Type: int32; R/W: R | O
Fixed Block |  | 34 | 32 | Size: 2; Name: int32_u; Type: int32; R/W: R | O
Fixed Block |  | 36 | 34 | 2 | uint32_1 |  |  | uint32 |  | sunssf_5 | R | O
Fixed Block |  | 38 | 36 | 2 | uint32_2 |  |  | uint32 |  | sunssf_6 | R | O
Fixed Block |  | 40 | 38 | 2 | uint32_3 |  |  | uint32 |  | sunssf_7 | RW | O
Fixed Block |  | 42 | 40 | 2 | uint32_4 |  |  | uint32 |  | 1 | R | O
Fixed Block |  | 44 | 42 | Size: 2; Name: uint32_5; Type: uint32; R/W: R | O
Fixed Block |  | 46 | 44 | Size: 2; Name: uint32_u; Type: uint32; R/W: R | O
Fixed Block |  | 48 | 46 | Size: 2; Name: acc32; Type: acc32; R/W: R | O
Fixed Block |  | 50 | 48 | Size: 2; Name: acc32_u; Type: acc32; R/W: R | O
Fixed Block |  | 52 | 50 | Size: 2; Name: enum32; Type: enum32; R/W: R | O
Fixed Block |  | 54 | 52 | Size: 2; Name: enum32_u; Type: enum32; R/W: R | O
Fixed Block |  | 56 | 54 | Size: 2; Name: bitfield32; Type: bitfield32; R/W: R | O
Fixed Block |  | 58 | 56 | Size: 2; Name: bitfield32_u; Type: bitfield32; R/W: R | O
Fixed Block |  | 60 | 58 | Size: 2; Name: ipaddr; Type: ipaddr; R/W: RW | O
Fixed Block |  | 62 | 60 | Size: 2; Name: ipaddr_u; Type: ipaddr; R/W: R | O
Fixed Block |  | 64 | 62 | Size: 4; Name: int64; Type: int64; R/W: RW | O
Fixed Block |  | 68 | 66 | Size: 4; Name: int64_u; Type: int64; R/W: R | O
Fixed Block |  | 72 | 70 | Size: 4; Name: acc64; Type: acc64; R/W: R | O
Fixed Block |  | 76 | 74 | Size: 4; Name: acc64_u; Type: acc64; R/W: R | O
Fixed Block |  | 80 | 78 | Size: 8; Name: ipv6addr; Type: ipv6addr; R/W: R | O
Fixed Block |  | 88 | 86 | Size: 8; Name: ipv6addr_u; Type: ipv6addr; R/W: R | O
Fixed Block |  | 96 | 94 | Size: 2; Name: float32; Type: float32; R/W: RW | O
Fixed Block |  | 98 | 96 | Size: 2; Name: float32_u; Type: float32; R/W: R | O
Fixed Block |  | 100 | 98 | Size: 16; Name: string; Type: string; R/W: RW | O
Fixed Block |  | 116 | 114 | Size: 16; Name: string_u; Type: string; R/W: R | O
Fixed Block |  | 132 | 130 | Size: 1; Name: sunssf_5; Type: sunssf; R/W: R | O
Fixed Block |  | 133 | 131 | Size: 1; Name: sunssf_6; Type: sunssf; R/W: R | O
Fixed Block |  | 134 | 132 | Size: 1; Name: sunssf_7; Type: sunssf; R/W: R | O
Fixed Block |  | 135 | 133 | Size: 1; Name: pad_1; Type: pad; R/W: R | O
Repeating Block |  | 136 | 0 | Size: 1; Name: sunssf_8; Type: sunssf; R/W: R | O
Repeating Block |  | 137 | 1 | 1 | int16_11 |  |  | int16 |  | sunssf_8 | RW | O
Repeating Block |  | 138 | 2 | 1 | int16_12 |  |  | int16 |  | sunssf_9 | R | O
Repeating Block |  | 139 | 3 | Size: 1; Name: int16_u; Type: int16; R/W: R | O
Repeating Block |  | 140 | 4 | 1 | uint16_11 |  |  | uint16 |  | sunssf_8 | RW | O
Repeating Block |  | 141 | 5 | 1 | uint16_12 |  |  | uint16 |  | sunssf_9 | R | O
Repeating Block |  | 142 | 6 | Size: 1; Name: uint16_13; Type: uint16; R/W: R | O
Repeating Block |  | 143 | 7 | Size: 1; Name: uint16_u; Type: uint16; R/W: R | O
Repeating Block |  | 144 | 8 | 2 | int32 |  |  | int32 |  | sunssf_1 | RW | O
Repeating Block |  | 146 | 10 | Size: 2; Name: int32_u; Type: int32; R/W: R | O
Repeating Block |  | 148 | 12 | 2 | uint32 |  |  | uint32 |  | sunssf_9 | RW | O
Repeating Block |  | 150 | 14 | Size: 2; Name: uint32_u; Type: uint32; R/W: R | O
Repeating Block |  | 152 | 16 | Size: 1; Name: sunssf_9; Type: sunssf; R/W: R | O
Repeating Block |  | 153 | 17 | Size: 1; Name: pad_2; Type: pad; R/W: R | O

## 63002
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | SunSpec Test Model 2 | 63002 | uint16 |  |  | R | M
Header |  | 1 |  | 1 | L |  | (RB Count * 4) | uint16 |  |  | R | M | Model Length
Repeating Block |  | 2 | 0 | Size: 1; Name: sunssf_1; Type: sunssf; R/W: R | O
Repeating Block |  | 3 | 1 | 1 | int16_1 |  |  | int16 |  | sunssf_1 | RW | O
Repeating Block |  | 4 | 2 | 1 | int16_2 |  |  | int16 |  | sunssf_2 | R | O
Repeating Block |  | 5 | 3 | Size: 1; Name: sunssf_2; Type: sunssf; R/W: R | O

## 64001
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Veris Status and Configuration | 64001 | uint16 |  |  | R | M
Header |  | 1 |  | 1 | L |  | 71 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | Cmd | Command Code |  | enum16 |  |  | RW | O
Fixed Block |  | 3 | 1 | 1 | HWRev | Hardware Revision |  | uint16 |  |  | R | O
Fixed Block |  | 4 | 2 | 1 | RSFWRev | RS FW Revision |  | uint16 |  |  | R | O
Fixed Block |  | 5 | 3 | 1 | OSFWRev | OS FW Revision |  | uint16 |  |  | R | O
Fixed Block |  | 6 | 4 | 2 | ProdRev | Product Revision |  | string |  |  | R | O
Fixed Block |  | 8 | 6 | 1 | Boots | Boot Count |  | uint16 |  |  | R | O
Fixed Block |  | 9 | 7 | 1 | Switch | DIP Switches |  | bitfield16 |  |  | R | O
Fixed Block |  | 10 | 8 | 1 | Sensors | Num Detected Sensors |  | uint16 |  |  | R | O
Fixed Block |  | 11 | 9 | 1 | Talking | Num Communicating Sensors |  | uint16 |  |  | R | O
Fixed Block |  | 12 | 10 | 1 | Status | System Status |  | bitfield16 |  |  | R | O
Fixed Block |  | 13 | 11 | 1 | Config | System Configuration |  | bitfield16 |  |  | R | O
Fixed Block |  | 14 | 12 | 1 | LEDblink | LED Blink Threshold |  | uint16 | Pct |  | R | O
Fixed Block |  | 15 | 13 | 1 | LEDon | LED On Threshold |  | uint16 | Pct |  | R | O
Fixed Block |  | 16 | 14 | Size: 1; Name: Reserved; Type: uint16; R/W: R | O
Fixed Block |  | 17 | 15 | 16 | Loc | Location String |  | string |  |  | R | O
Fixed Block |  | 33 | 31 | 1 | S1ID | Sensor 1 Unit ID |  | enum16 |  |  | R | O
Fixed Block |  | 34 | 32 | 1 | S1Addr | Sensor 1 Address |  | uint16 |  |  | R | O
Fixed Block |  | 35 | 33 | 1 | S1OSVer | Sensor 1 OS Version |  | uint16 |  |  | R | O
Fixed Block |  | 36 | 34 | 2 | S1Ver | Sensor 1 Product Version |  | string |  |  | R | O
Fixed Block |  | 38 | 36 | 5 | S1Serial | Sensor 1 Serial Num |  | string |  |  | R | O
Fixed Block |  | 43 | 41 | 1 | S2ID | Sensor 2 Unit ID |  | enum16 |  |  | R | O
Fixed Block |  | 44 | 42 | 1 | S2Addr | Sensor 2 Address |  | uint16 |  |  | R | O
Fixed Block |  | 45 | 43 | 1 | S2OSVer | Sensor 2 OS Version |  | uint16 |  |  | R | O
Fixed Block |  | 46 | 44 | 2 | S2Ver | Sensor 2 Product Version |  | string |  |  | R | O
Fixed Block |  | 48 | 46 | 5 | S2Serial | Sensor 2 Serial Num |  | string |  |  | R | O
Fixed Block |  | 53 | 51 | 1 | S3ID | Sensor 3 Unit ID |  | enum16 |  |  | R | O
Fixed Block |  | 54 | 52 | 1 | S3Addr | Sensor 3 Address |  | uint16 |  |  | R | O
Fixed Block |  | 55 | 53 | 1 | S3OSVer | Sensor 3 OS Version |  | uint16 |  |  | R | O
Fixed Block |  | 56 | 54 | 2 | S3Ver | Sensor 3 Product Version |  | string |  |  | R | O
Fixed Block |  | 58 | 56 | 5 | S3Serial | Sensor 3 Serial Num |  | string |  |  | R | O
Fixed Block |  | 63 | 61 | 1 | S4ID | Sensor 4 Unit ID |  | enum16 |  |  | R | O
Fixed Block |  | 64 | 62 | 1 | S4Addr | Sensor 4 Address |  | uint16 |  |  | R | O
Fixed Block |  | 65 | 63 | 1 | S4OSVer | Sensor 4 OS Version |  | uint16 |  |  | R | O
Fixed Block |  | 66 | 64 | 2 | S4Ver | Sensor 4 Product Version |  | string |  |  | R | O
Fixed Block |  | 68 | 66 | 5 | S4Serial | Sensor 4 Serial Num |  | string |  |  | R | O

## 64020
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Mersen GreenString | 64020 | uint16 |  |  | R | M
Header |  | 1 |  | 1 | L |  | 30 + (RB Count * 16) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | Aux0Tmp | Aux 0 temperature |  | int16 | C |  | R | O
Fixed Block |  | 3 | 1 | 1 | Aux1Tmp | Aux 1 temperature |  | int16 | C |  | R | O
Fixed Block |  | 4 | 2 | 1 | Aux2Tmp | Aux 2 temperature |  | int16 | C |  | R | O
Fixed Block |  | 5 | 3 | 1 | Aux3Tmp | Aux 3 temperature |  | int16 | C |  | R | O
Fixed Block |  | 6 | 4 | 1 | Aux4Tmp | Aux 4 temperature |  | int16 | C |  | R | O
Fixed Block |  | 8 | 6 | 1 | ProbeTmp | Probe Temperature |  | int16 | C |  | R | M
Fixed Block |  | 7 | 5 | 1 | MainTmp | Main Temperature |  | int16 | C |  | R | M
Fixed Block |  | 9 | 7 | 1 | SensorV_SF | Voltage scale factor for the sensors |  | sunssf |  |  | R | M
Fixed Block |  | 10 | 8 | 1 | SensorA_SF | Current scale factor for the sensors |  | sunssf |  |  | R | M
Fixed Block |  | 11 | 9 | 1 | SensorHz_SF | Frequency scale factor for the sensors |  | sunssf |  |  | R | M
Fixed Block |  | 12 | 10 | 1 | Sensor1Voltage | Sensor1 Voltage |  | int16 | V | SensorV_SF | R | O | scale of 0-10V
Fixed Block |  | 13 | 11 | 1 | Sensor2Voltage | Sensor2 Voltage |  | int16 | V | SensorV_SF | R | O | scale of 0-10V
Fixed Block |  | 14 | 12 | 1 | Sensor3Voltage | Sensor3 Voltage |  | int16 | V | SensorV_SF | R | O | scale of 0-10V
Fixed Block |  | 15 | 13 | 1 | Sensor4Voltage | Sensor4 Voltage |  | int16 | V | SensorV_SF | R | O | scale of 0-10V
Fixed Block |  | 16 | 14 | 1 | Sensor5Voltage | Sensor5 Voltage |  | int16 | V | SensorV_SF | R | O | scale of 0-10V
Fixed Block |  | 17 | 15 | 1 | Sensor6Voltage | Sensor6 Voltage |  | int16 | V | SensorV_SF | R | O | scale of 0-10V
Fixed Block |  | 18 | 16 | 1 | Sensor7Voltage | Sensor7 Voltage |  | int16 | V | SensorV_SF | R | O | scale of 0-10V
Fixed Block |  | 19 | 17 | 1 | Sensor1Current | Sensor1 Current |  | int16 | A | SensorA_SF | R | O | scale of 4-20mA
Fixed Block |  | 20 | 18 | 1 | Sensor2Current | Sensor2 Current |  | int16 | A | SensorA_SF | R | O | in 4-20mA or 4-20mA
Fixed Block |  | 21 | 19 | 1 | Sensor3Current | Sensor3 Current |  | int16 | A | SensorA_SF | R | O | in 4-20mA or 4-20mA
Fixed Block |  | 22 | 20 | 1 | Sensor4Current | Sensor4 Current |  | int16 | A | SensorA_SF | R | O | in 4-20mA or 4-20mA
Fixed Block |  | 23 | 21 | 1 | Sensor5Current | Sensor5 Current |  | int16 | A | SensorA_SF | R | O | in 4-20mA or 4-20mA
Fixed Block |  | 24 | 22 | 1 | Sensor6Current | Sensor6 Current |  | int16 | A | SensorA_SF | R | O | in 4-20mA or 4-20mA
Fixed Block |  | 25 | 23 | 1 | Sensor7Current | Sensor7 Current |  | int16 | A | SensorA_SF | R | O | in 4-20mA or 4-20mA
Fixed Block |  | 26 | 24 | 1 | Sensor8 | Sensor8 frequency |  | uint16 | Hz | SensorHz_SF | R | O | frequency in Hz
Fixed Block |  | 27 | 25 | 1 | Relay1 | Relay 1 state |  | uint16 |  |  | R | O
Fixed Block |  | 28 | 26 | 1 | Relay2 | Relay 2 state |  | uint16 |  |  | R | O
Fixed Block |  | 29 | 27 | 1 | Relay3 | Relay 3 state |  | uint16 |  |  | R | O
Fixed Block |  | 30 | 28 | 1 | ResetAccumulators | Reset the accumulators |  | uint16 |  |  | R | O | always 0 in reading, used the code 0xC0DA during the writting for resetting them
Fixed Block |  | 31 | 29 | 1 | Reset | Reset the system |  | uint16 |  |  | R | O | always 0 in reading, used the code 0xC0DA during the writting for resetting the system
Repeating Block |  | 32 | 0 | 9 | SerialNumber | Serial number |  | string |  |  | R | M | strings of 16 caracters
Repeating Block |  | 41 | 9 | 6 | Firmware | Firmware version |  | string |  |  | R | M | string of 11 caracters
Repeating Block |  | 47 | 15 | 1 | Hardware | Hardware version |  | uint16 |  |  | R | M

## 64101
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Eltek Inverter Extension | 64101 | uint16 |  |  | R | M
Header |  | 1 |  | 1 | L |  | 7 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | Size: 1; Name: Eltek_Country_Code; Type: uint16; R/W: R | O
Fixed Block |  | 3 | 1 | Size: 1; Name: Eltek_Feeding_Phase; Type: uint16; R/W: R | O
Fixed Block |  | 4 | 2 | Size: 1; Name: Eltek_APD_Method; Type: uint16; R/W: R | O
Fixed Block |  | 5 | 3 | Size: 1; Name: Eltek_APD_Power_Ref; Type: uint16; R/W: R | O
Fixed Block |  | 6 | 4 | Size: 1; Name: Eltek_RPS_Method; Type: uint16; R/W: R | O
Fixed Block |  | 7 | 5 | Size: 1; Name: Eltek_RPS_Q_Ref; Type: uint16; R/W: R | O
Fixed Block |  | 8 | 6 | Size: 1; Name: Eltek_RPS_CosPhi_Ref; Type: int16; R/W: R | O

## 64110
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | OutBack AXS device | 64110 | uint16 |  |  | R | M
Header |  | 1 |  | 1 | L |  | 282 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | MajorFWRev | AXS Major Firmware Number |  | uint16 |  |  | R | M
Fixed Block |  | 3 | 1 | 1 | MidFWRev | AXS Mid Firmware Number |  | uint16 |  |  | R | M
Fixed Block |  | 4 | 2 | 1 | MinorFWRev | AXS Minor Firmware Number |  | uint16 |  |  | R | M
Fixed Block |  | 5 | 3 | 1 | EncrypKey | Encryption Key |  | uint16 |  |  | R | M
Fixed Block |  | 6 | 4 | 7 | MAC_Address | MAC Address |  | string |  |  | R | M
Fixed Block |  | 13 | 11 | 8 | WritePassword | Write Password |  | string |  |  | R | M
Fixed Block |  | 21 | 19 | 1 | EnableDHCP | Enable DHCP |  | enum16 |  |  | R | M
Fixed Block |  | 22 | 20 | 2 | TCPIP_address | TCPIP Address |  | ipaddr |  |  | R | M
Fixed Block |  | 24 | 22 | 2 | Gateway_address | TCPIP Gateway |  | ipaddr |  |  | R | M
Fixed Block |  | 26 | 24 | 2 | TCPIP_Netmask | TCPIP Netmask |  | ipaddr |  |  | R | M
Fixed Block |  | 28 | 26 | 2 | DNS1_address | TCPIP DNS1 |  | ipaddr |  |  | R | M
Fixed Block |  | 30 | 28 | 2 | DNS2_address | TCPIP DNS2 |  | ipaddr |  |  | R | M
Fixed Block |  | 32 | 30 | 1 | Modbus_port | ModBus Port |  | uint16 |  |  | R | M
Fixed Block |  | 33 | 31 | 20 | SMTP_server_nm | SMTP Server Name |  | string |  |  | R | M
Fixed Block |  | 53 | 51 | 16 | SMTP_account_nm | SMTP Account Name |  | string |  |  | R | M
Fixed Block |  | 69 | 67 | 1 | SMTP_enable_SSL | Enable SMTP SSL |  | enum16 |  |  | R | M
Fixed Block |  | 70 | 68 | 8 | SMTP_password | SMTP Password |  | string |  |  | R | M
Fixed Block |  | 78 | 76 | 20 | SMTP_user_nm | SMTP User Name |  | string |  |  | R | M
Fixed Block |  | 98 | 96 | 1 | Stat_email_int | Status Email Interval |  | uint16 |  |  | R | M
Fixed Block |  | 99 | 97 | 1 | Stat_start_HR | Status Email Start Hour |  | uint16 |  |  | R | M
Fixed Block |  | 100 | 98 | 25 | Stat_email_sub | Status Email Subject |  | string |  |  | R | M
Fixed Block |  | 125 | 123 | 20 | Stat_email_addr1 | Status Email to Address 1 |  | string |  |  | R | M
Fixed Block |  | 145 | 143 | 20 | Stat_email_addr2 | Status Email to Address 2 |  | string |  |  | R | M
Fixed Block |  | 165 | 163 | 1 | Alarm_email_en | Enable Alarm Email |  | enum16 |  |  | R | M
Fixed Block |  | 166 | 164 | 25 | Alarm_email_sub | Alarm Email Subject |  | string |  |  | R | M
Fixed Block |  | 191 | 189 | 20 | Alarm_email_addr1 | Alarm Email to Address 1 |  | string |  |  | R | M
Fixed Block |  | 211 | 209 | 20 | Alarm_email_addr2 | Alarm Email to Address 2 |  | string |  |  | R | M
Fixed Block |  | 231 | 229 | 8 | FTP_password | FTP Password |  | string |  |  | R | M
Fixed Block |  | 239 | 237 | 8 | TELNET_password | Telnet Password |  | string |  |  | R | M
Fixed Block |  | 247 | 245 | 1 | Log_write_int | SD-Card Datalog Write Interval |  | uint16 | Tms |  | R | M
Fixed Block |  | 248 | 246 | 1 | Log_retain | SD-Card Datalog Retain |  | uint16 | Tmd |  | R | M
Fixed Block |  | 249 | 247 | 1 | Log_mode | SD-Card Datalog Mode |  | enum16 |  |  | R | M
Fixed Block |  | 250 | 248 | 20 | NTP_server_nm | NTP Timer Server Name |  | string |  |  | R | M
Fixed Block |  | 270 | 268 | 1 | NTP_enable | Enable Network Time |  | enum16 |  |  | R | M
Fixed Block |  | 271 | 269 | 1 | TimeZone | Time Zone |  | int16 | Tmh |  | R | M
Fixed Block |  | 272 | 270 | 1 | Date_year | Year |  | uint16 |  |  | R | M
Fixed Block |  | 273 | 271 | 1 | Date_month | Month |  | uint16 |  |  | R | M
Fixed Block |  | 274 | 272 | 1 | Date_Day | Day |  | uint16 |  |  | R | M
Fixed Block |  | 275 | 273 | 1 | Time_hour | Hour |  | uint16 |  |  | R | M
Fixed Block |  | 276 | 274 | 1 | Time_minute | Minute |  | uint16 |  |  | R | M
Fixed Block |  | 277 | 275 | 1 | Time_second | Second |  | uint16 |  |  | R | M
Fixed Block |  | 278 | 276 | 1 | Battery_temp | Battery Temperature |  | int16 | C | Temp_SF | R | M
Fixed Block |  | 279 | 277 | 1 | Ambient_temp | Ambient Temperature |  | int16 | C | Temp_SF | R | M
Fixed Block |  | 280 | 278 | Size: 1; Name: Temp_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 281 | 279 | 1 | AXS_Error | AXS Error |  | bitfield16 |  |  | R | M
Fixed Block |  | 282 | 280 | 1 | AXS_Status | AXS Status |  | bitfield16 |  |  | R | M
Fixed Block |  | 283 | 281 | 1 | AXS_Spare | Spare |  | uint16 |  |  | R | M
enum16 | SMTP_enable_SSL |  |  | Name: ASX_DISABLED; Label: Disabled; Value: 0
enum16 | SMTP_enable_SSL |  |  | Name: ASX_ENABLED; Label: Enabled; Value: 1
enum16 | Alarm_email_en |  |  | Name: ASX_DISABLED; Label: Disabled; Value: 0
enum16 | Alarm_email_en |  |  | Name: ASX_ENABLED; Label: Enabled; Value: 1
enum16 | Log_mode |  |  | Name: LOG_DISABLED; Label: Disabled; Value: 0
enum16 | Log_mode |  |  | Name: LOG_EXCEL; Label: Excel; Value: 1
enum16 | Log_mode |  |  | Name: LOG_COMPACT; Label: Compact; Value: 2
enum16 | NTP_enable |  |  | Name: ASX_DISABLED; Label: Disabled; Value: 0
enum16 | NTP_enable |  |  | Name: ASX_ENABLED; Label: Enabled; Value: 1

## 64111
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Basic Charge Controller | 64111 | uint16 |  |  | R | M
Header |  | 1 |  | 1 | L |  | 23 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | Port | Port Number |  | uint16 |  |  | R | M
Fixed Block |  | 3 | 1 | Size: 1; Name: V_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 4 | 2 | Size: 1; Name: A_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 5 | 3 | Size: 1; Name: P_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 6 | 4 | Size: 1; Name: AH_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 7 | 5 | Size: 1; Name: KWH_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 8 | 6 | 1 | BattV | Battery Voltage |  | uint16 | V | V_SF | R | M
Fixed Block |  | 9 | 7 | 1 | ArrayV | Array Voltage |  | uint16 | V | V_SF | R | M
Fixed Block |  | 10 | 8 | 1 | OutputA | Output Current |  | uint16 | A | A_SF | R | M
Fixed Block |  | 11 | 9 | 1 | InputA | Array Current |  | uint16 | A | P_SF | R | M
Fixed Block |  | 12 | 10 | 1 | ChargerSt | Operating State |  | enum16 |  |  | R | M
Fixed Block |  | 13 | 11 | 1 | OutputW | Output Wattage |  | uint16 | W | P_SF | R | M
Fixed Block |  | 14 | 12 | 1 | TodayMinBatV | Todays Minimum Battery Voltage |  | uint16 | V | V_SF | R | M
Fixed Block |  | 15 | 13 | 1 | TodayMaxBatV | Todays Maximum Battery Voltage |  | uint16 | V | V_SF | R | M
Fixed Block |  | 16 | 14 | 1 | VOCV | VOC |  | uint16 | V | V_SF | R | M
Fixed Block |  | 17 | 15 | 1 | TodayMaxVOC | Todays Maximum VOC |  | uint16 | V | V_SF | R | M
Fixed Block |  | 18 | 16 | 1 | TodaykWhOutput | Todays kWh |  | uint16 | kWh | KWH_SF | R | M
Fixed Block |  | 19 | 17 | 1 | TodayAHOutput | Todays AH |  | uint16 | AH | AH_SF | R | M
Fixed Block |  | 20 | 18 | 1 | LifeTimeKWHOut | Lifetime kWh |  | uint16 | kWh | P_SF | R | M
Fixed Block |  | 21 | 19 | 1 | LifeTimeAHOut | Lifetime kAH |  | uint16 | kAH | KWH_SF | R | M
Fixed Block |  | 22 | 20 | 1 | LifeTimeMaxOut | Lifetime Maximum Output Wattage |  | uint16 | W | P_SF | R | M
Fixed Block |  | 23 | 21 | 1 | LifeTimeMaxBatt | Lifetime Maximum Battery Voltage |  | uint16 | V | V_SF | R | M
Fixed Block |  | 24 | 22 | 1 | LifeTimeMaxVOC | Lifetime Maximum VOC Voltage |  | uint16 | V | V_SF | R | M
enum16 | ChargerSt |  |  | Name: Off; Label: Off; Value: 0
enum16 | ChargerSt |  |  | Name: Float; Label: Float Charging; Value: 1
enum16 | ChargerSt |  |  | Name: Bulk; Label: Bulk Charging; Value: 2
enum16 | ChargerSt |  |  | Name: Absorb; Label: Absorb Charging; Value: 3
enum16 | ChargerSt |  |  | Name: EQ; Label: Equilize Charging; Value: 4

## 64112
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | OutBack FM Charge Controller | 64112 | uint16 |  |  | R | M
Header |  | 1 |  | 1 | L |  | 64 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | Port | Port Number |  | uint16 |  |  | R | M
Fixed Block |  | 3 | 1 | Size: 1; Name: V_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 4 | 2 | Size: 1; Name: C_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 5 | 3 | Size: 1; Name: H_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 6 | 4 | Size: 1; Name: P_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 7 | 5 | Size: 1; Name: AH_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 8 | 6 | Size: 1; Name: KWH_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 9 | 7 | 1 | CC_Config_fault | Faults |  | bitfield16 |  |  | R | M
Fixed Block |  | 10 | 8 | 1 | CC_Config_absorb_V | Absorb |  | uint16 | V | V_SF | R | M
Fixed Block |  | 11 | 9 | 1 | CC_Config_absorb_Hr | Absorb Time |  | uint16 | Tmh | H_SF | R | M
Fixed Block |  | 12 | 10 | 1 | CC_Config_absorb_End_A | Absorb End |  | uint16 | A | V_SF | R | M
Fixed Block |  | 13 | 11 | 1 | CC_Config_rebulk_V | Rebulk |  | uint16 | V | V_SF | R | M
Fixed Block |  | 14 | 12 | 1 | CC_Config_float_V | Float |  | uint16 | V | V_SF | R | M
Fixed Block |  | 15 | 13 | 1 | CC_Config_max_Chg_A | Maximum Charge |  | uint16 | A | V_SF | R | M
Fixed Block |  | 16 | 14 | 1 | CC_Config_equalize_V | Equalize |  | uint16 | V | V_SF | R | M
Fixed Block |  | 17 | 15 | 1 | CC_Config_equalize_Hr | Equalize Time |  | uint16 | Tmh |  | R | M
Fixed Block |  | 18 | 16 | 1 | CC_Config_auto_equalize | Auto Equalize Interval |  | uint16 | Tmd |  | R | M
Fixed Block |  | 19 | 17 | 1 | CC_Config_MPPT_mode | MPPT mode |  | enum16 |  |  | R | M
Fixed Block |  | 20 | 18 | 1 | CC_Config_sweep_width | Sweep Width |  | enum16 |  |  | R | M
Fixed Block |  | 21 | 19 | 1 | CC_Config_sweep_max | Sweep Maximum |  | enum16 |  |  | R | M
Fixed Block |  | 22 | 20 | 1 | CC_Config_U_Pick_Duty_cyc | U-Pick PWM Duty Cycle |  | uint16 | Pct | V_SF | R | M
Fixed Block |  | 23 | 21 | 1 | CC_Config_grid_tie | Grid Tie Mode |  | enum16 |  |  | R | M
Fixed Block |  | 24 | 22 | 1 | CC_Config_temp_comp | Temp Comp Mode |  | enum16 |  |  | R | M
Fixed Block |  | 25 | 23 | 1 | CC_Config_temp_comp_llimt | Temp Comp Lower Limit |  | uint16 | V | V_SF | R | M
Fixed Block |  | 26 | 24 | 1 | CC_Config_temp_comp_hlimt | Temp Comp Upper Limit |  | uint16 | V | V_SF | R | M
Fixed Block |  | 27 | 25 | 1 | CC_Config_auto_restart | Auto Restart Mode |  | enum16 |  |  | R | M
Fixed Block |  | 28 | 26 | 1 | CC_Config_wakeup_VOC | Wakeup VOC Change |  | uint16 | V | V_SF | R | M
Fixed Block |  | 29 | 27 | 1 | CC_Config_snooze_mode_A | Snooze Mode |  | uint16 | A | V_SF | R | M
Fixed Block |  | 30 | 28 | 1 | CC_Config_wakeup_interval | Wakeup Interval |  | uint16 | Tms |  | R | M
Fixed Block |  | 31 | 29 | 1 | CC_Config_AUX_mode | AUX Output Mode |  | enum16 |  |  | R | M
Fixed Block |  | 32 | 30 | 1 | CC_Config_AUX_control | AUX Output Control |  | enum16 |  |  | R | M
Fixed Block |  | 33 | 31 | 1 | CC_Config_AUX_state | AUX Output State |  | enum16 |  |  | R | M
Fixed Block |  | 34 | 32 | 1 | CC_Config_AUX_polarity | AUX Output Polarity |  | enum16 |  |  | R | M
Fixed Block |  | 35 | 33 | 1 | CC_Config_AUX_L_Batt_disc | AUX Low Battery Disconnect |  | uint16 | V | V_SF | R | M
Fixed Block |  | 36 | 34 | 1 | CC_Config_AUX_L_Batt_rcon | AUX Low Battery Reconnect |  | uint16 | V | V_SF | R | M
Fixed Block |  | 37 | 35 | 1 | CC_Config_AUX_L_Batt_dly | AUX Low Battery Disconnect Delay |  | uint16 | Tms |  | R | M
Fixed Block |  | 38 | 36 | 1 | CC_Config_AUX_Vent_fan_V | AUX Vent Fan |  | uint16 | V | V_SF | R | M
Fixed Block |  | 39 | 37 | 1 | CC_Config_AUX_PV_triggerV | AUX PV Trigger |  | uint16 | V | V_SF | R | M
Fixed Block |  | 40 | 38 | 1 | CC_Config_AUX_PV_trg_h_tm | AUX PV Trigger Hold Time |  | uint16 | Tms |  | R | M
Fixed Block |  | 41 | 39 | 1 | CC_Config_AUX_Nlite_ThrsV | AUX Night Light Threshold |  | uint16 | V | V_SF | R | M
Fixed Block |  | 42 | 40 | 1 | CC_Config_AUX_Nlite_On_tm | AUX Night Light On Time |  | uint16 | Tmh | H_SF | R | M
Fixed Block |  | 43 | 41 | 1 | CC_Config_AUX_Nlite_On_hist | AUX Night Light On Hysterisis |  | uint16 | Tms |  | R | M
Fixed Block |  | 44 | 42 | 1 | CC_Config_AUX_Nlite_Off_hist | AUX Night Light Off Hysterisis |  | uint16 | Tms |  | R | M
Fixed Block |  | 45 | 43 | 1 | CC_Config_AUX_Error_batt_V | AUX Error Output Low Battery |  | uint16 | V | V_SF | R | M
Fixed Block |  | 46 | 44 | 1 | CC_Config_AUX_Divert_h_time | AUX Divert Hold Time |  | uint16 | Tms | V_SF | R | M
Fixed Block |  | 47 | 45 | 1 | CC_Config_AUX_Divert_dly_time | AUX Divert Delay Time |  | uint16 | Tms |  | R | M
Fixed Block |  | 48 | 46 | 1 | CC_Config_AUX_Divert_Rel_V | AUX Divert Relative |  | uint16 | V | V_SF | R | M
Fixed Block |  | 49 | 47 | 1 | CC_Config_AUX_Divert_Hyst_V | AUX Divert Hysterisis |  | uint16 | V | V_SF | R | M
Fixed Block |  | 50 | 48 | 1 | CC_Config_MajorFWRev | FM CC Major Firmware Number |  | uint16 |  |  | R | M
Fixed Block |  | 51 | 49 | 1 | CC_Config_MidFWRev | FM CC Mid Firmware Number |  | uint16 |  |  | R | M
Fixed Block |  | 52 | 50 | 1 | CC_Config_MinorFWRev | FM CC Minor Firmware Number |  | uint16 |  |  | R | M
Fixed Block |  | 53 | 51 | 1 | CC_Config_DataLog_Day_offset | Set Data Log Day Offset |  | uint16 | Tmd |  | R | M
Fixed Block |  | 54 | 52 | 1 | CC_Config_DataLog_Cur_Day_off | Current Data Log Day Offset |  | uint16 | Tmd |  | R | M
Fixed Block |  | 55 | 53 | 1 | CC_Config_DataLog_Daily_AH | Data Log Daily |  | uint16 | Ah |  | R | M
Fixed Block |  | 56 | 54 | 1 | CC_Config_DataLog_Daily_KWH | Data Log Daily |  | uint16 | kWh | KWH_SF | R | M
Fixed Block |  | 57 | 55 | 1 | CC_Config_DataLog_Max_Out_A | Data Log Daily Maximum Output |  | uint16 | A | V_SF | R | M
Fixed Block |  | 58 | 56 | 1 | CC_Config_DataLog_Max_Out_W | Data Log Daily Maximum Output |  | uint16 | W | V_SF | R | M
Fixed Block |  | 59 | 57 | 1 | CC_Config_DataLog_Absorb_T | Data Log Daily Absorb Time |  | uint16 | Tms |  | R | M
Fixed Block |  | 60 | 58 | 1 | CC_Config_DataLog_Float_T | Data Log Daily Float Time |  | uint16 | Tms |  | R | M
Fixed Block |  | 61 | 59 | 1 | CC_Config_DataLog_Min_Batt_V | Data Log Daily Minimum Battery |  | uint16 | V | V_SF | R | M
Fixed Block |  | 62 | 60 | 1 | CC_Config_DataLog_Max_Batt_V | Data Log Daily Maximum Battery |  | uint16 | V | V_SF | R | M
Fixed Block |  | 63 | 61 | 1 | CC_Config_DataLog_Max_Input_V | Data Log Daily Maximum Input |  | uint16 | V | V_SF | R | M
Fixed Block |  | 64 | 62 | 1 | CC_Config_DataLog_Clear | Data Log Clear |  | uint16 |  |  | R | M
Fixed Block |  | 65 | 63 | 1 | CC_Config_DataLog_Clr_Comp | Data Log Clear Complement |  | uint16 |  |  | R | M
enum16 | CC_Config_MPPT_mode |  |  | Name: Auto; Label: Auto; Value: 1
enum16 | CC_Config_MPPT_mode |  |  | Name: U_Pick; Label: U-Pick; Value: 1
enum16 | CC_Config_MPPT_mode |  |  | Name: Wind; Label: Wind; Value: 2
enum16 | CC_Config_sweep_width |  |  | Name: Half; Label: Half; Value: 0
enum16 | CC_Config_sweep_width |  |  | Name: Full; Label: Full; Value: 1
enum16 | CC_Config_sweep_max |  |  | Name: Eighty_Percent; Label: 80 %; Value: 0
enum16 | CC_Config_sweep_max |  |  | Name: Eighty_Five_Percent; Label: 85 %; Value: 1
enum16 | CC_Config_sweep_max |  |  | Name: Ninty_Percent; Label: 90 %; Value: 2
enum16 | CC_Config_sweep_max |  |  | Name: Ninty_Nine_Percent; Label: 99 %; Value: 3
enum16 | CC_Config_grid_tie |  |  | Name: Disabled; Label: Disabled; Value: 0
enum16 | CC_Config_grid_tie |  |  | Name: Enabled; Label: Enabled; Value: 1
enum16 | CC_Config_temp_comp |  |  | Name: Wide; Label: Wide; Value: 0
enum16 | CC_Config_temp_comp |  |  | Name: Limited; Label: Limited; Value: 1
enum16 | CC_Config_auto_restart |  |  | Name: Off; Label: Off; Value: 0
enum16 | CC_Config_auto_restart |  |  | Name: Every_90_Minutes; Label: Every 90 Minutes; Value: 1
enum16 | CC_Config_auto_restart |  |  | Name: Every_90_Minutes_if_Absorb_or_Float; Label: Every 90 Minutes if Absorb or Float; Value: 2
enum16 | CC_Config_AUX_mode |  |  | Name: Float; Label: Float; Value: 0
enum16 | CC_Config_AUX_mode |  |  | Name: Diversion_Relay; Label: Diversion: Relay; Value: 1
enum16 | CC_Config_AUX_mode |  |  | Name: Diversion_Solid_St; Label: Diversion: Solid St; Value: 2
enum16 | CC_Config_AUX_mode |  |  | Name: Low_Batt_Disconnect; Label: Low Batt Disconnect; Value: 3
enum16 | CC_Config_AUX_mode |  |  | Name: Remote; Label: Remote; Value: 4
enum16 | CC_Config_AUX_mode |  |  | Name: Vent_Fan; Label: Vent Fan; Value: 5
enum16 | CC_Config_AUX_mode |  |  | Name: PV_Trigger; Label: PV Trigger; Value: 6
enum16 | CC_Config_AUX_mode |  |  | Name: Error_Output; Label: Alarm Output; Value: 7
enum16 | CC_Config_AUX_mode |  |  | Name: Night_Light; Label: Night Light; Value: 8
enum16 | CC_Config_AUX_control |  |  | Name: Off; Label: Off; Value: 0
enum16 | CC_Config_AUX_control |  |  | Name: Auto; Label: Auto; Value: 1
enum16 | CC_Config_AUX_control |  |  | Name: On; Label: On; Value: 2
enum16 | CC_Config_AUX_state |  |  | Name: Disabled; Label: Disabled; Value: 0
enum16 | CC_Config_AUX_state |  |  | Name: Enabled; Label: Enabled; Value: 1
enum16 | CC_Config_AUX_polarity |  |  | Name: Low; Label: Low; Value: 0
enum16 | CC_Config_AUX_polarity |  |  | Name: High; Label: High; Value: 1